DIO POLICY INSTRUCTION			Estate Management
Subject: KITCHEN BUILD PROJECTS AND CATERING EQUIPMENT STANDARDS ON THE MOD ESTATE / Number: PI 2022 - 01
Technical Services Sponsor: Bryan Dunn		Date of issue: 11 January 2022
Contact if different from above Sponsor: / Environmental Health Team / Defence Infrastructure Organisation / St George’s House, DMS(W), Whittington Barracks, Lichfield, WS14 9PY
Who should read this: DIO Personnel, Public, Private Partnerships, Private Finance Initiatives, Contractors and Project Managers / Commercial Officers involved in the procurement of commercial catering equipment and refurbishment or new build projects on the MOD estate that involve kitchens or catering outlets.
When it takes effect: Immediately	When it is due to expire: until updated or rescinded

Equality and Diversity Impact Assessment

This policy has been Equality and Diversity Impact Assessed in accordance with the Department’s Equality and
Diversity Impact Assessment Tool against:

Part 1 Assessment Only (no diversity impact found)

DOCUMENT AIM

1. To clarify the DIO policy for the standard of finishes, services and equipment in MOD kitchens and catering facilities and the process for engagement with DIO Technical Services Environmental Health Team (EHT). This document details the minimum requirement and standards for infrastructure finishes, services and equipment for MOD commercial catering facilities, in addition to the requirements of the legislation. EHT processes are detailed at the end of this policy.

2. DMG 18 and Specification 42 legacy documents have been reviewed, rescinded and incorporated into this policy document.

DOCUMENT TO BE READ IN CONJUNCTION WITH

A	JSP 850 Part 2 Building Performance Standards.
B	JSP 456 Defence Catering Manual.

POLICY AND STATUTORY REQUIREMENTS
3. This policy applies to all catering / kitchen infrastructure and food equipment replacements on the MOD estate (UK and Overseas) from the date of policy publication.

4.	All catering infrastructure and food equipment replacements will be reviewed by DIO Technical Services Environmental Health Team against the following standards providing the following advice.

Standard	Type of advice provided by EHT
Food Safety legislation Regulation (EC) 852/2004	Statutory advice
Food Safety legislation Regulation (EC) 178/2002	Statutory advice
Health and Safety at Work etc. Act 1974	Statutory advice
Provision and Use of Work Equipment Regulations 1998	Statutory advice
JSP 315 Service Accommodation Code	Mandatory advice
JSP 850 Infrastructure and Estate Policy Standards and Guidance	Mandatory advice
JSP 456 The Defence Catering Manual	Mandatory advice
Building Performance Standard 2.1 Catering	Mandatory advice

PURPOSE AND APPLICABILITY

5.	The use of this document is mandatory. This document details the minimum requirements and standards for infrastructure finishes, services, and equipment for MOD commercial catering facilities. Reference should also be made to JSP 456 Defence Catering Manual.

6.	The use of this document should ensure consistency across the estate, promoting value for money and assuring fitness for purpose, whilst supporting compliance with health and safety and food safety legislation. The DIO Technical Services Environmental Health Team must be consulted on all new or proposed alterations to commercial catering infrastructure on the estate. This is to provide technical guidance to TLBs.
TECHNICAL APPLICATION
Kitchen Design Principles

7.	Legislation sets out in detail the requirements for all food premises. To set these in architectural and building terms, the design and construction of all food premises must:

Allow the building to be kept clean and maintained in good condition and repair.

Enable adequate cleaning and/or disinfection.

Provide prevention against the accumulation of dirt, contact with toxic materials and the shedding of particles into food.

Inhibit the formation of condensation or mould.

Facilitate good hygiene practices.

Provide appropriate temperature conditions for the processing and storage of foods.

Provide protection from contamination – by foodstuffs, equipment, materials, water, personnel or pests.

Preparation areas should be separated to prevent cross contamination.

Finishes and Services

8.	This section defines the minimum standards, services and finishes required for MOD catering facilities. Where it is proposed to deviate from these standards, a Determination must be sought from DIO Technical Services Environmental Health Team, who hold the Technical Authority for catering infrastructure on the MOD estate.

a.	Floors

	In addition to being able to be maintained in a sound condition, be impervious, non-absorbent and constructed of a suitable material.

	Slip resistant even when wet, easy to maintain, clean and disinfect.

	Designed and installed to accommodate the intended activity, reinforced where necessary in high traffic areas.

	Any grout, silicone or filling compound must be finished flush to the surface of the floor covering and itself be easy to clean and disinfect, not shed or crack, and be compatible and appropriate to the floor covering laid.

	Where possible, must not incorporate raised plinths or open channels.

	Installed in accordance with the manufacturer’s recommendations installers guidance.

	Floor coverings between the floor and wall junctions and wall corners must be continuous/coved to the wall.

	Must not require specialist cleaning techniques or equipment to maintain in a clean condition. Replacement floor finishes must be compatible with the cleaning techniques employed by the contractor.

b.	Walls

	In addition to being able to be maintained in a sound condition, be impervious, non-absorbent, and constructed of a suitable material to facilitate cleaning.

	Any grout, silicone or filling compound must be finished flush to the surface of the wall covering and itself be easy to clean and disinfect, not shed or crack and be compatible and appropriate to the wall covering installed.

	Finishes to internal walls (including impact protection) must be constructed of non-toxic materials, washable, and of smooth surface to a height appropriate for the operation and must be easy to maintain, clean and disinfect.

	Must not easily shed or fragment, especially in food preparation areas.

	Edges to tiles, hygienic clad or other protruding surface must be finished with an edging strip, flush to the surface and itself be able to be cleaned and disinfected.

	Where necessary, exposed corners and wall surfaces must be fitted with impact protection to an appropriate height to minimise surface damage.

c.	Ceilings and Overhead Fixtures

	Must be designed, constructed, and finished to prevent the accumulation of dirt, reduce condensation and mould growth and not shed particles.

	Must be non-combustible, smooth, impervious and easy to clean and maintain.

	All service pipes, trunking and other penetrations must be caulked and sealed.

	Where ventilated ceilings are installed, the grid system must be followed and where filters are removed for cleaning, each filter must be returned to the same location (usually marked with an identification code) to ensure that ventilation panels are not blocked by solid panels.

d.	Doors

	Doors and frames must be robust, able to withstand heavy use and have a smooth easy-to-clean finish.

	Hardware / ironmongery such as hinges, panels and handles must be constructed of corrosion resistant smooth materials and be capable of being cleaned and disinfected.

	Doors must be fitted flush to the frame to prevent gaps allowing pest entry. Any gaps to the bottom of doors must be fitted with a bristle / rubber strip or suitable alternative to allow the free passage of the door, whilst preventing pest access.

	Bevelled edges must be kept to a minimum, be smooth finished, free of protruding fixings and be able to be effectively cleaned.

	Where large or heavy trolleys or hand operated pallet trucks are used, adequate impact protection must be fitted to doors and door frames, to a suitable height on the door to prevent damage.

	All access doors must allow movement of large mobile catering equipment and replacements.

	Where possible, window panels should be avoided in external delivery doors and impact	protection should be installed to a height to take account of cages, roll racks etc.

	In all working and preparation areas doors must be fitted with an appropriate vision panel to avoid collision hazards.

	Servery doors should be two way opening into servery areas.

e.	Windows

	In addition to being able to be maintained in a sound condition, be impervious, non-absorbent, and constructed of a suitable material.

	Fly screens should be fitted on all openable windows in all food handling areas, where there is a possibility of flying pest access or where situated near to waste holding areas.

	Where fly screens are installed, they must be capable of being easily removed by hand, to assist cleaning and must not comprise protruding fixings.

	Any hardware or fixings to window openings must be of corrosion free materials to permit cleaning and disinfection.

	Where possible, windows should not be incorporated in dedicated refrigeration areas.

	Consideration should be given to the intended layout and type of equipment within rooms, to reduce glare and heat transfer through glazing.

f.	Drainage

	Adequate drainage must be provided to allow effective wash down of the infrastructure in preparation areas and to receive discharge from cooking appliances separately.

	Drainage services must be located so, as to minimise damage from impact (e.g., mobile equipment), must be of a durable material and allow access for cleaning.

	Gullies, trays, and gratings must be durable and accessible for cleaning, and able to be lifted to remove debris.

	Where walk-in refrigeration and air-cooling plant is installed, drainage must be provided to accept the defrost condensate externally.

	Drainage components must be constructed of materials that are smooth and able to be effectively cleaned.

	In hard water areas, consideration should be given to the impact of scale formation and measures installed to prevent early failure of components.

	Pipework joins must be kept to a minimum and fitted flush to prevent residue and dirt accumulation around the join.

g.	Grease Interception

	The design of drainage must take due cognizance of the treatment of fats, oils and grease (FOG) by either physical or biological means.

	Grease interception must be provided in ware washing areas and kitchen cooking suites.

	Grease interception points and channels must be able of being removed and emptied easily, without the need for specialist tools and constructed in a way to prevent physical contamination with solid waste other than FOGs.

	Grease interception points must be sited away from areas where there could be a possibility of either physical debris or chemical contamination, which could impact on the effectiveness of the interception points. This is particularly applicable where biological methods are incorporated.

h.	Water

	An adequate supply of potable hot and cold water must be provided.

	Cooking equipment requiring water connections must be fitted with flexible final service connections and quick disconnect valves.

	Treated, conditioned potable drinking water, by a food-safe method must be supplied to combination ovens, steaming ovens, beverage making equipment and water boilers.

	Water fed cooking equipment must be fitted with water softening and / or filters appropriate to the water hardness for the location. Softening units / filters must incorporate visible indicators and be accessible to be exchanged.

	Where conditioning apparatus is sited adjacent to equipment, the apparatus must be installed in a manner to permit the surrounding area to be cleaned and not interfere with the safe operation of the equipment being supplied.

i.	Electrical services

	A sufficient number of electrical sockets must be provided in all preparation areas, for portable equipment.

	All sockets must be located at a suitable height for food handlers to access.

	Electrical sockets within food preparation rooms must have the appropriate IP protection, relative to the tasks being carried out.

	Where practical, sockets and switches must be flush mounted with impact resistant facias.

	Additional electrical sockets must be provided for mobile cleaning equipment at not less than 12m intervals.

	In dining areas, double sockets must be provided to every 37m2 of floor space within entrance / exit lobbies and queue spaces.

	Electrical distribution boards should be sited away from food preparation areas, to permit any maintenance activities to take place outside of food rooms.

j.	Lighting

	Consideration must be given to the activities undertaken within all rooms, to ensure adequate lighting provision for food handlers to carry out tasks safely.

	Lighting housing must be constructed to prevent any source of contamination into foodstuffs, particularly in the event of bulb breakage, which must be contained within the housing.

	Light fixings must be secured without protruding fixings and where possible, be flush mounted.

	Lights must be accessible and be capable of being cleaned and emptied of debris, flying insects and dust.

	External weatherproof lighting must be provided at entrances, loading, refuse and external catering activity areas.

k.	Ventilation

	Catering facilities must have sufficient natural or mechanical ventilation, commensurate to the production activities and type of equipment provided.

	All heat producing equipment must have adequate mechanical extraction ventilation, determined by a specialist ventilation engineer.

	A suitably qualified ventilation specialist must be consulted during the design process to determine appropriate ventilation requirements.

	Ceiling / wall fitted ventilation must be constructed and installed to enable filters and parts that require cleaning to be accessed with ease and replaced as necessary.

	Ventilation filters must be capable of being easily removed without the need for specialist tools and be easily cleanable.

	Ventilation systems must not create excessive noise or odour nuisance.

l.	Extraction Canopies

	Dedicated extraction canopies with appropriate filters must be provided to prime cooking equipment, dishwasher, utensil washer, water boilers and gas fired equipment, unless already fitted with internal heat recovery systems.

	Extraction canopies must overlay the footprint or equipment/working area below, in accordance with HSE guidance.

	Extraction canopies above deep fat frying equipment should be designed and installed with consideration to fire suppression, in accordance with Fire Standards. Specific advice can be obtained from the project fire officer.

	All components and fittings must be easily removable without the need of special tools.

m.	Pest Control

	The design and layout of catering facilities must prevent access to pests.

	All gaps / voids in walls, floors, ceilings and around drains must be suitably permanently sealed.

	All gaps to doors must be pest proofed using flexible seals or brush strips.

	Where installed, insect killers must be located at strategic points, to control winged pests and not situated above food preparation, equipment or food storage areas.

	Waste must be segregated, and defunct equipment and materials must not be stored in a manner which is likely to attract pests.

CATERING AREAS – LAYOUT AND DESIGN

9.	General

	Kitchen and ancillary areas must, where possible, be located at ground floor with direct level access for deliveries. Where not at ground level, access must be provided to allow the safe transfer of stock and equipment and removal of waste.

10.	Spatial Standards

	JSP 850 Building Performance Standard 2.1 Catering, must be consulted for permitted spatial allowances and equipment frequencies for all dedicated food areas.

	Where a project requires different spatial standards, robust technical justification must be provided and approved by the Technical Authority EHT. A Determination application is required as per the EHT Determination process.

	Spatial standards for the feeding band must be followed, except for where refurbishment of existing facilities exceeds the allowance provided by the BPS 2.1.

	All spatial standards within the BPS 2.1 incorporate a work activity area associated with the specific item of equipment and include door opening circles.

	Spatial standards are based on activities relevant to site. Where rooms are not required, there is no automatic entitlement e.g., pastry area not entitled if all desserts are purchased ready to eat, sandwich packing room not entitled where packed meals are not provided etc.

	Consideration must be given to spacing equipment away from heat sources, ventilation grids, etc., and suiting prime appliances in areas with dedicated extraction ventilation.

Adequate set down tabling must be provided within prime cooking suites, where there are runs
of catering equipment, to ensure trays and vessels being removed from cooking appliances can be safely stowed.

Where necessary, supplied equipment should be mobile to facilitate cleaning and maintenance.

Space should be allocated for non GFE project specific equipment and caterer provided items, within preparation rooms e.g., waste receptacles, recycling points etc.

11.	Kitchen

	Where necessary, equipment should be mobile to facilitate cleaning and maintenance.

	A centralised kitchen serving different messes, whilst maintaining segregation between differing ranks is the default design scheme.

Preparation areas including raw meat, vegetable prep, larder, pastry etc. are to be clearly defined
areas. Separate rooms will only be provided where there is justification for the specific activities being isolated and where there is sufficient staff resource to utilise those spaces.

All food preparation areas must contain a wash hand basin, waste receptacle and sink.

Raw preparation areas must be appropriately sited to ensure that cross contamination is avoided. Separation may be achieved through the strategic placement of equipment and, where necessary, mid height walls to provide structural segregation.

Where pastry preparation is provided in a separate dedicated room with adequate drainage must be provided to all cooking appliances.
12.	Crockery wash / Utensil wash

	The crockery wash must be sited with direct access to the waste area, without passing through	a food preparation area.

	Crockery and utensil washes should be provided in a combined room, unless restricted by spatial or racking capacity.

Most dishwashers can be provided with heat recovery and do not require a dedicated extraction ventilation canopy. However, where the model being installed does not have an integrated system or there are poor ventilation levels within the room, an extraction ventilation canopy will be required to extract steam and heat from the area.

The area must have adequate drainage gullies or soak away to ensure that water does not pool in the area. Drainage facilities must be accessible, easy to clean and able to be removed to unblock any debris.

Dishwashers must be installed leaving a gap around the appliance, to permit effective cleaning of the surrounding infrastructure.

Where possible, the use of ceiling tiles in the crockery wash area should be avoided. Where a suspended ceiling requires the use of ceiling tiles, these must be constructed of waterproof materials that avoid mould formation. The grid system holding the tiles must also be corrosion resistant, washable material.

13.	Grocery Store

	Must be self-contained and capable of being secured.

	Must be sited close to the loading/unloading area.

	Where applicable, access to the store and the circulation space must be wide enough to accept palletised deliveries.

	The area must be well ventilated. Heat emanating from refrigeration plant must be removed through adequate air changes.

	Unless on braked wheels or runners, racking must be secured to the ground with fixings that do not protrude.

	Racking must be sited to permit the surrounding area to be cleaned.

	Racking must be adequately spaced, to provide suitable staff working space, to stack and retrieve items, using safe methods of work.

	A suitable number of power sockets should be provided to support freestanding refrigeration and freezer cabinets.

Where out of hours access is required to the store, the store should be located so that passage through the main kitchen or preparation areas is not required to access the storeroom.

The storeroom should be sited near to the waste area, to permit waste packaging and cardboard to be discarded, without having to travel through food preparation rooms.

14.	External Service Area

	Level access should be provided for the safe unloading of goods.

	A cold-water point, drainage gully and electricity supply must be provided.

	A secured area must be provided for the storage of waste.

	Waste oil must be stored in suitably secured bunded pest proofed containers.

15.	Norwegian Container Wash (where provided)

	Norwegian rooms are only permitted for training units that feed ‘in the field’.

	The location of Norwegian rooms must enable receipt of dirty Norwegian containers, direct from the 'field' to be emptied and washed without entering a food room.

	Reference should be made to BPS 2.1, for sink and racking provision for the area.

	Adequate floor drainage gullies must be installed to allow direct discharge from sinks and to assist floor cleaning procedures.

	Racking must be securely fixed with adequate room to carry out cleaning.

16.	Packed Meal Room (where provided)

	Must be self-contained and located to allow the collection of packed meals, without accessing the rest of the catering area

	Consideration should be given to the proximity of the packed meal room to the consumables store area, unless packaging etc is to be stored on racking within the room.

SERVERY AND DINING AREAS

17.	Servery

	Doors must swing through 180° with a dedicated in / out traffic flow.

	The Officers’ and SNCOs’ serveries are normally separated from the dining room and must be adaptable to self-service operations.

18.	Back Bar (where provided)

	Back bar facilities are provided only where there is a ‘cook to order ‘or theatre cooking menu options.

	The project fire officer must be consulted regarding the need to install fire suppression measures for any fat frying equipment in the area.

19.	Cleaners / COSHH Store

	A wall hanging rack or similar must be supplied to hang mops and brushes after washing and allow for separation of cleaning equipment.

	Wall protection must be provided to prevent damage to the wall from equipment or chemical spillage/staining.

	A suitable janitorial or drainage unit must be provided for the disposal of dirty water and used chemicals.
Hand washing facilities must be provided.

	Provision must be made for the bulk storage of cleaning chemicals and materials which must be kept secure.

	A suitable number of electrical sockets must be provided to the room.

BARS AND CELLARS

20.	JSP 315 must be consulted regarding the provision of bar facilities and:

	The bar, servery and cellar must be constructed of smooth, impervious coverings / surfaces, fixtures, and fittings.
	An adequate hot and cold potable water supply must be provided.

	A dedicated wash hand basin and separate sink, for decanting and swilling glasses,
  prior to washing must be provided.

	Suitable glass washing facilities must be provided in accordance with JSP 315.

	A potable water supply and suitable drainage must be provided to ice machines.

	A separate general store area must be provided, for the storage of ancillary bar items.

	Adequate ventilation must be provided to cellars, to prevent the build-up of moulds and yeast spores on walls and ceilings.

	Floor finishes in cellar storage areas must be sufficiently robust to allow for the movement of kegs / barrels and large crates.

The policy requirement is to provide a finished infrastructure only.

Bar design, fridges, merchandising equipment, and ancillaries are funded and specified by the TLB charity or contractor, depending on the operational management of the bar facility.

EQUIPMENT SPECIFICATIONS
Introduction

21.	This section defines the minimum mandated standards required for catering equipment on the MOD estate. In addition to the legal requirements, supplied catering equipment must be suitable for medium duty use in a commercial catering operation. Equipment provision is directed by BPS 2.1 and based on entitled feeding strength. Any deviation must be requested via a Determination application to the Technical Authority and be supported by robust technical evidence to justify the request. Advice will be provided by EHT.

General Equipment Specification Prerequisites

22.	All equipment supplied to MOD establishments shall be constructed to comply with all relevant legislation and British Standards and:

	Must be commercial grade, fit for purpose, and be constructed of materials that can be kept clean, in good condition and repair, and are corrosion resistant.

	Be made from robust hard-wearing material, which is smooth, impervious, easy to clean and disinfect, and does not pose risks of contamination.

	Where mobile, the front castors to the equipment must be braked.

	Be installed to allow ease of access for maintenance and cleaning of the infrastructure.

	Exposed surfaces of equipment should be free of rivet heads, screws, and bolts to enable effective cleaning and disinfection.

	Fixings must not pose a risk of contamination.

	Where necessary, be appropriately guarded and not be able to be easily tampered.

	Prime cooking equipment must have commonality of depth and finished working height.

	All elements within the following areas should be from a common manufacturer, to achieve continuity, operational safety, and ease of maintenance.

 -	crock wash,	-	refrigeration	-	servery counters

Fabricated Equipment

23.	Benching / supporting stands

	Benching must be free-standing.

	Wall benching must have an appropriate upstand free from sharp edges.

	Dishwasher tabling must have height adjustable feet.

24.	Racking / dunnage and shelving

	Shelves must be suitable for the intended use and load.

	Be free of rivet heads, screws, indents and smooth surfaced to prevent the accumulation of dirt and debris and permit cleaning and disinfection.

	Supporting legs must be solid, smooth and easy to clean, not trap dirt or debris and be capable of being maintained in a clean condition.

25.	Sinks

	A potable hot and cold-water supply must be provided.

	A rear upstand and smooth drainer must be provided.

	Bowl size must be adequately dimensioned to accommodate a GN 1/1 container.

26.	Inset sinks (crock and utensil wash areas)

	Taps must be set back to allow uninterrupted movement of loaded racks.

	The inlet tabling must have adequate depth and height to suit ware wash machine entry / exit.

	Tabling must be profiled to form a rack guide.

	Must have a suitable smoothed upstand to prevent the falling of items from racking and food debris behind the equipment.

27.	Hot cupboard/servery counter

	A dry heat blown air heating system must be incorporated.

	The minimum holding temperature must allow food to be kept no cooler than 63°C.

	The cupboard must be of sufficient depth to accommodate a GN 1/1 lengthways.

	Doors must be insulated.

	Doors must be removable and top hung.

	Consideration must be given to the need to provide a tray slide to the servery counter.

	Where possible, be mobile to permit transport to dining rooms.

28.	Wash hand basins

	Must be wall hung.

	Any gap between the wash hand basin and wall surface must be suitably sealed.

	Must be located to avoid cross contamination e.g., away from waste receptacles, raw foods etc.

      	A splash back must be provided to protect the wall covering, which is appropriately sealed and provides a smooth, cleanable surface.

	Hot and cold-water supply must be via a mixer tap or thermostatically controlled at the outlet.

	Adequate wall space must be provided to install soap and paper towel dispensers within close proximity of the basin.

Adequate space should be provided for a waste receptacle to receive used paper towels within the vicinity of the wash hand basin, without blocking access to it.

PRIME COOKING EQUIPMENT

29.	Fat fryer

	A suitable number of steel wire frying baskets must be provided with the unit.

	Each fry pan must be provided with a lift off lid.

	The access door must be side hinged.

	Independent temperature controls must be provided for each pan.

	Must have a temperature safety thermostat.

30.	Grill

	Installation must be at a suitable operating height.

	Sufficient runners must be provided to allow varying grilling levels.

	Be bench mounted, fixed to the bench with non-protruding fixings.

	Must be provided with suitable set down space to allow the grill tray to be rested.

	A spillage / fat collection tray must be provided.

31.	Combination oven

	Must be capable of holding as a minimum a GN 1/1 40 mm deep container on each runner.

	6 and 10 shelf units must be mounted on a suitable stand.

	An automatic water supply and drain down facility must be incorporated.

	Doors must be side hung.

	A condense channel must be integrated into the door.

	Fan and elements / burners must cut out when the door is opened.

	The oven must be capable of operating on a minimum of convection, combination, steaming and regeneration modes and include a pre-heat function.

	An automatic cleaning system with a minimum of two wash levels, rinse and auto switch off is required.

	Be provided with a water filter / softener.

Purchased with a year’s supply of cleaning tablets.

32.	Range and Boiling table

	Ovens must be able to accommodate two GN 1/1 side by side.

	Each hotplate / burner must be independently controlled.

33.	Induction hob / wok

	Units must be of heavy-duty construction.

	An automatic shut off function is required.

	A clean filter warning indicator is required.

	A warm surface indicator is required.

	Each unit must be supplied with an induction compatible pan set.

34.	Pressure Steamer

	The pressure vessel must have an in-built steam generator.

	The unit must be able to accommodate 3 x GN 1/1 containers.

	The pan support system must be removable for cleaning.

	An automatic draining facility is required.

	A low water alarm and safety cut off feature must be included.

	A stand must be supplied to support the steamer with GN containers on runners beneath.

	Be provided with water filter / softener.

35.	Atmospheric convection steamer

	This item must be considered where a pressure steamer cannot be installed or where menu output dictates.

	A low water alarm and safety cut off feature must be included.

	Each unit must be supplied with 6 shelves.

	Where required, be provided with water filter / softener.

REFRIGERATION

36.	Refrigerator and freezers

	Refrigerators must be commercial grade and capable of storing high risk foods below 8°C.

	Walk in chillers and freezers are not supported by policy, except for unique technical reasoning. This allows contingency in the event of failure and supports sustainability and cost effectiveness.

	Refrigeration provision is provided by free standing cabinets as set out in BPS 2.1.

	Free standing units must be mobile, with braked wheels.

	Where storing valuable goods, or sited in rooms accessed out of hours, units must be capable of being locked.

	The interior of cabinets must be able to accommodate GN 1/1 and GN 2/1 containers.

	Automatic defrost with vaporisation is required.

	A temperature display / warning system must be included.

	Must be robust, with easily cleanable door seals.

	Where refrigerated counters are required, these must accommodate GN 1/1 containers.

37.	Walk in cold rooms (where already installed or provided)

	All surfaces including floor must be constructed of materials that permit cleaning and disinfection.

	Adequate automatic internal lighting must be provided, which activates when the door is opened.

	The entrance door must be capable of being opened from the inside.

	An emergency escape mechanism must be provided to permit door release from the inside.

	Racking must be securely fixed and installed to permit cleaning to the rear of the racking.

38.	Blast chiller / freezer

	Blast chillers are only provided to facilities with large feeding strengths or surge feeding. Refer to BPS 2.1.

	Units must accept GN 1/1 containers.

	A digital display showing temperature, stage in cycle, and time to completion is required.

	An appropriate number of shelves must be provided.

	Must be mobile with braked wheels.

PREPARATION EQUIPMENT

39.	All preparation equipment (mixer, peeler, veg prep machine) must be:

	Commercial grade versions, able to withstand heavy use.

	Constructed of smooth, impervious, easily cleanable materials.

	Fixings must not present a risk of detachment and contamination.

	Demountable parts must be guarded but easily removable without the need for special tools.

	Base units must be rigid and of a suitable weight to maintain stability.

	If used for dual purpose (raw and ready to eat foods) equipment must be fully demountable and	be capable of being washed in a dishwasher and disinfected between uses.

	All mobile equipment provided must be commercial grade e.g., toasters, microwaves etc.

	All mobile (plug in and play) equipment provided by the contractor or self-funded must comply with these policy requirements.

40.	Instantaneous Water boilers

	Units must be automatic fill from a potable cold-water supply.

	Units must be suitable for counter installation (reinforcement may be required to counter).

	Units must include a thermostatically controlled immersion heater designed to maintain a constant 98°C.

	Units must incorporate low water, boil dry and high temperature cut out systems.

	The overflow connection must be to the rear of the equipment and drain directly to the drainage system.

	An easily accessible drain plug must be incorporated to allow complete drain down of the boiler.

	Access for maintenance must be at the front of the unit.

	The discharge tap must be positioned at a height which permits adequate clearance to permit the safe filling of vessels beneath, including coffee pots, Norwegian containers etc.

	Where required, a drip tray with a removable grid must be provided and where suitable must drain into the drainage system. Note this is in addition to the required to drain directly into the system.

	Consideration should be given to the water hardness and a de-scaling regime implemented to prevent early equipment failure due to scale build up.

Floor standing boiling kettles were removed from policy several years ago. All instantaneous boiling water requirements are to be drawn from instantaneous water heaters.

WAREWASHING

41.	Combined Dishwasher / Utensil washer / plate washer

	Dishwashers must have a minimum wash water temperature of 60°C, final rinse 82°C.

	Pass through hood dishwashers must provide an output of 60 racks per hour: rack conveyor dishwashers a minimum of 100 racks per hour.

	Controls must be easily accessible and readable.

	A thermal lock must be incorporated to ensure appropriate temperature is met for each cycle.

	Rack conveyor dishwashers must be fitted with an air-drying tunnel.

	Racks must be robust, durable, and able to withstand heat and chemicals.

	Internal accessories must be removable for cleaning, without the need for special tools.

There must be adequate access to the internal machine to permit debris and chemical build removal and descaling.

	Utensil washers must incorporate as a minimum a 120 second and a continuous operation cycle.
42.	Glass washer (where provided)

	Glass washers are not government funded but where provided, must comply with these policy requirements.

	Glass washer must be front loading.

	Glass washer wash temperature must be 55°C and 65°C rinse water temperature.

	The minimum cycle required for glass washers is 60 seconds.

	Consideration should be given to the water hardness and a de-scaling regime implemented to prevent early equipment failure due to scale build up.

MAINTENANCE

43.	Kitchen managers are responsible for ensuring that catering facilities are kept in a clean condition, regularly cleansed and sanitised, in accordance with legal responsibilities and JSP 456.

44.	Kitchen managers are responsible for ensuring soft maintenance tasks, including equipment cleaning are carried out frequently, combination oven and dishwasher clean cycles are programmed regularly, using the appropriate tablets, and water softener filters are monitored and replaced regularly.

45.	Extraction ventilation filters and external surfaces of extraction ventilation ducting are to be cleaned by the SFM provider, in accordance with the SFM contract.

46.	All internal extraction ventilation ducting and pipework, motor and areas beyond the filters are to be deep cleaned in accordance with MOD SFG20 modules by the HFM contractor.

47.	Equipment defects and failures are to be reported by the kitchen / mess manager without delay, and every effort taken to enable access and support the contractor to undertake inspections and repairs as required.

48.	Where repaired equipment remains in an unusable condition, it is the responsibility of the contractor, with support from DIO Regional Delivery, to follow up action to ensure the equipment is brought back into service or replaced without undue delay. Subject to TLB funding approval.

49.	Where infrastructure defects are identified e.g., flaking paint, damaged pipework, ceiling mould etc. either by the SFM contractor, Local Authority or Military Environmental Health; the defects are to be reported without delay. With DIO RD support, and subject to TLB funding approval a works request must be raised to ensure the infrastructure defect(s) is / are resolved without unreasonable delay.

50.	Electric winged insect killers require regular bulb maintenance. This is the responsibility of the HFM contractor. If the SFM contractor notices that the bulb is defective or out of service, they are to report to the HFM contractor for action.

51.	Where pest proofing becomes damaged or defective, it is the kitchen managers responsibility to raise the issue with the unit and Chain of Command to prompt repair works to be undertaken.

WASTE MANAGEMENT

52.	All kitchen waste is to be handled, managed, and disposed of in accordance with the legislative requirements and waste policies. This may vary depending on geographical location. Ensure that the kitchen is familiar with the local requirements including provision of waste receptacles for segregated waste.

53.	All waste should be managed in line with the waste hierarchy (avoid, reduce, re-use etc) moving away from disposal and where possible food waste should be avoided.

54.	Food macerators and bio-digesters were taken out of policy some time ago and their use is not supported. Food waste should be minimised and limited as far as practicably possible, using waste management strategies, to avoid the need to dispose of large volumes of food waste.

55.	The area around food waste bins both internally and externally must be kept free of debris and cleaned on a regular basis.

56.	The kitchen manager is responsible for ensuring that external waste areas are kept in clean and tidy condition and for raising any concerns with the unit, through the chain of command.

57.	All units must have an appropriate contract in place for the removal of waste cooking oil, which must be stored in a suitably pest proofed, bunded oil store prior to collection.

58.	Bunded waste oil stores must be managed, kept in clean condition and in a good state of repair.

59.	Any spillages of waste oil around to the vicinity of the waste oil store, or to the external catering area must be cleaned using a detergent product, to remove pathway contamination and potential slipping hazards.

60.	Beyond Economic Repair (BER) and defunct catering equipment must be disposed of in accordance with waste rules. The MOD DESA can be contacted to arrange disposal or reselling of life cycle equipment replacements.

61.	Defunct equipment must not be stored in catering areas or externally to catering areas, as this provides harbourage for pests.

62.	The kitchen manager is to report to the QM or unit contact, to ensure that catering equipment is appropriately stored prior to disposal. All equipment must be moved to a designated store if there is likely to be delay to an appropriate waste transfer.

63.	All relevant compliance documentation, for example waste transfer notices and consignment notes must be stored in accordance with the legislative requirements.

64.	Refer to JSP850, 478 Leaflet 3 and JSP456 Part 2 vol 3 for detailed waste requirements.

SUSTAINABILITY

65.	MOD, like many other organisations has a sustainability plan. The impact on catering is that cooking, and	refrigeration equipment is becoming more energy efficient. Where possible, consideration should be given to energy efficient models that offer long term value for money.

66.	Many units are moving away from gas fuelled appliances, to reduce fossil fuel consumption and replacing with electrical equivalents. Where such replacements are planned, electrical capacity must be assessed to ensure that any increased capacity can be accommodated.

67.	Refer to JSP850 for standards and guidance relating to sustainability.

ENVIRONEMNTAL HEALTH TEAM PROJECT ENGAGEMENT PROCESSES

68. BER process

69. PROJECT process

70. DETERMINATION process

OTHER INFORMATION SOURCES

Related Statute
Food Hygiene (England) Regulations 2013
Regulation (EC) 852/2004 / R
Regulation (EC) 178/2002
Health and Safety at Work etc. Act 1974 / Provision and Use of Work Equipment Regulations 1998

Related JSPs Title
JSP 315 Service Accommodation Code
JSP 850 Infrastructure and Estate Policy Standards and Guidance
JSP 456 The Defence Catering Manual

Related Guidance Title
Building Performance Standard 2.1 Catering

GLOSSARY

Abbreviations, terms and definitions.

BPS means Building Performance Standards.

Catering Areas means the catering areas where food is delivered, stored, prepared, cooked, served, likely to be transported and includes ware washing facilities and equipment storage.

CGL means crockery, glass and linen store.

COSHH means control of substances hazardous to health.

CRL means catering, retail and leisure facility.

DESA means the Defence Equipment Sales Authority.

EH means Environmental Health.

EHT means Environmental Health Team.

Determination means a formal request made by the Project Team to the EH team to deviate from the minimum standards contained within this document.

DMG means Defence and Maintenance Guide.

FOG means fats, oil and grease.

FOH means front of house.

GFE means Government Funded Equipment.

GN means Gastronorm container. A GN container is a cooking vessel of various sizes 1/1 etc.

HFM means Hard Facilities Manager(ment).

HSE means Health and Safety Executive.

JSP means Joint Service Publication.

Kitchen Equipment Inventory is a list of equipment within the facility.

MOD means Ministry of Defence.

NTBF means numbers to be fed, which is derived from those entitled to use the mess facilities.

QM means Quartermaster / OC Supply / OC Logistics.

RD means Regional Delivery.

SFG20 means the industry standard for building maintenance specifications.

SFM means Soft Facilities Manager(ment).

Technical Authority is the definitive authority for commercial catering infrastructure design, standards and equipment on the MOD estate and is held by the DIO EHT.

TLB means Top Level Budget holder.

VFM means Value for Money.