Technical Standard: Automatic Fire Detection and suppression in Dwellings Occupied by MOD Personnel.
Technical Standard Fire 2022/03 Replaces PI 10-05	ESTATE MANAGEMENT

Version 1.0 – 2022/03

Document Information
DIO Sponsor: Bryan Dunn	Date of Issue: 01 Feb 2022
Contact if different from above Sponsor: / DIO TS Senior Fire Safety Manager, / Defence Infrastructure Organisation, / Kingston Road, Sutton Coldfield B75 7RL. / DIO-TSFiresafety@mod.gov.uk
MOD telephone: Mobile: 07790 960334 / Email: DIO-TSFiresafety@mod.gov.uk
Who should read this: DIO, TLB and other Personnel involved in management of housing on the Defence Estate, Defence safety personnel involved in risk assessment of this type of accommodation, Fire risk assessors, Heads of Establishments and site/Regional Health and Safety Advisors.
When it takes effect: Immediately	When it is due to expire: When Rescinded
Equality and Diversity Impact Assessment: / This policy has been Equality and Diversity Impact Assessed in accordance with the Defence Equality Analysis Guidance 2018 up to: / Part 1 Assessment Only (no diversity impact found) / This Document replaces the previous PI: PI 05/10

Document Name:	Policy instruction: Automatic Fire Detection in Dwellings occupied by MOD personnel.
Version No:	V1.0
Version Date:	01 February 2022
Author:	DIO TS SFSM Marc Plester
Reviewed by:	Bryan Dunn Head of TS Engineering and Construction
Review Date:	12 months from publishing

Document History
Date Issued	Version	Author	Reason for Change
01 Feb 2022	1.0	Marc Plester	Review and update for consultation. This document supersedes DIO PI 05/10 which will be redacted

Foreword
This Policy Instruction here after known as ‘the Standard’ is published by Defence Infrastructure Organisation (DIO) for Mandatory application across all areas of the MoD. This standard is mandated for all contracts including USVF, overseas and PFI arrangements.
Document Synopsis
The aim of this Policy Instruction is to provide guidance and direction on how to ensure fire safety requirements are consistently achieved, where Defence agencies or personnel hold responsibility, for the use of dwellings/quarters and privately let properties by MOD personal.

Contents
Roles and Implementation
………………………………….…………………………………………………………………………………….……………………….………4
Application of Policy Instruction
………………………..……………………………………………………………………………………………………………………………… 4
References
………………………………………………………………………………………………………………………………………………………...5
Glossary of terms
……………………………….…………………………………………………………………………………………………………..…………5/6

1. Roles and Implementation
  1. DIO are the document owner and Technical Authority for this standard. Approval for any deviation or derogation from this standard is be approved by the DIO Senior Fire Safety Manager prior to the commencement of any work or change of use. DIO-TSFireSafety@mod.gov.uk
  2. Under the Regulatory Reform Order (fire Safety) 2005 at present there is no requirement to have a Fire risk assessment on a domestic dwelling that is being considered for occupancy by MOD personnel, however it is recommended that any landlords should supply a document that should include any identified specific risks from fire to the Client.
  3. These standards are to be retrospectively applied in Scotland in accordance with the legislation, systems should be upgraded to properties fitted outside Scotland as soon as reasonably practical to this Standard.

1. Application of the Policy Instruction
  1. This Policy Instruction applies to all domestic properties, leased or rented accommodation that will be occupied by MOD personal on or around the MOD estate.
  2. The property must be provided with a minimum Grade F1 LD2 interlinked and powered fire detection system in accordance with British Standard 5839 Part 6.
  3. An alternative to mains 240V powered is to have 10 year “fit-and-forget” battery operated interlinked detector system, which are maintenance free and connected by wireless communications, either are acceptable on the Estate.
  4. Any property where the occupant is known to have hearing difficulties may also have a requirement for additional specialist alert (vibration/visual) equipment to be linked to the system, and a risk assessment prior to occupation must be carried out to ensure suitable systems are fitted in consultation with DIO RD Accn.
  5. Any fire safety systems fitted to the property must before any occupancy/tenancy period starts, be tested by the Responsible Person for correct operation of all components of the system, and repairs/alterations/detector replacement/battery changes and maintenance completed as required.
  6. Kitchens must be fitted with a heat detector. Smoke detectors must be fitted to all stories in the premises on which a room including a bathroom, lavatory, hall, landing or reception room is used wholly or partly as living accommodation by the tenant and in all circulation spaces and reception rooms and the Principal bedroom (LD2+ coverage)
  7. Carbon monoxide detectors, which are supplementary to the smoke detectors and interlinked with the other detectors in the system, must be equipped in any room of the premises which is used wholly or partly as a living accommodation and contains a solid or oil fuel burning combustion appliance (such as a log burner, open fireplace or oil fed AGA type oven etc)
  8. If a property has photovoltaic systems (solar panels) fitted to the roof with inverters installed, then suitable interlinked detectors are to be installed to cover this additional potential hazard in the area where the electrical inverters/equipment is installed, but it is accepted that an end user will not monthly test if fitted in the loft area but only annually tested by the IP due to access.
  9. The energising batteries in the detectors must be changed in accordance with the manufacturer’s instruction, or if they start to “chirp” due to low battery status.
  10. The battery-operated smoke and heat detectors will need to be periodically replaced at or around the ten-year point and at seven years for carbon monoxide detectors by the Responsible Person, in accordance with manufacturer’s instructions.
  11. Detectors should be tested by the occupier in accordance with government recommended advice which is currently once a month.
  12. Sound levels from the detectors/sounders, fitted to landings/corridor ceilings on the floor where sleeping takes place, should be produced of at least 85dB in the bedroom doorways with the door open. This should give a sufficient sound at the bedhead of 75dB to rouse sleeping occupants when the average bedroom door is shut, unless the bedrooms are fitted with sounders, or the doors are particularly solid.
  13. It is noted that under Welsh Legislation domestic properties are to be fitted with sprinkler systems in new builds and major refurbishments, this is not as yet to be a wider provision across Defence outside of Wales.

3 References
British Standard 5839 Part 6, latest version
LACORS- Guidance on fire safety provisions for certain types of existing housing produced by the Local Authorities Coordinators of Regulatory Services latest version

# 4 Glossary of terms
Accn	Accommodation
BS 5839 Part 6	British Standard – Code of practice for the design, installation, commissioning and maintenance of fire detection and fire alarm systems in domestic premises.
CFR	Capita Fire & Rescue
DFR	Defence Fire & Rescue
DIO	Defence Infrastructure Organisation
dB	A measurement of the amount of sound in decibels (dB)
FAP	Fire Action Poster displayed to outlining the emergency actions to be taken by occupants in the event of a fire/fire alarm activation.
FRA	Fire Risk Assessment to indicate potential risks/hazards to the occupants during a fire.
Final Exit	The end of an escape route from a building that gives direct access to a street, walkway or open space of ultimate safety, and is sited to ensure that people rapidly disperse away from the building so not in danger from fire and smoke or collapse.
HoE	Head of Establishment
LACORS	Local authorities Coordinators of Regulatory services, outlining non statutory guidance on fire safety provisions for certain types of existing housing. / Currently v1.0 2008 which is under review.
F1 LD2	A grade and category of fire alarm system designed in accordance with BS 5839 that has a specific designed coverage of a building.
MoD	Ministry of Defence
Means of Escape	Structural means that provide one or more safe routes for people to go, during a fire, from any point in the building to a place of safety.
RD	Regional Delivery
SFA	Service Family Accommodation
SLA	Single Living Accommodation
Note:	Where the term “Must or shall” is used, this is a legislative legal or MOD policy requirement where the term “Should” is used, this is seen as industry wide best practice.

End of document.