## Revision & Guidance Notes
OFFSHORE COMBUSTION INSTALLATIONS POLLUTION PREVENTION & CONTROL (PPC) REGULATIONS 2013 (AS AMENDED)
STACK EMISSION MONITORING PLAN - PROFORMA
Purpose: This proforma is provided for operators to manage compliance monitoring under their PPC permit for Large Combustion Plant (LCP) and Medium Combustion Plant (MCP). The annual monitoring plan requirement for LCP is a condition in the PPC permit. The monitoring plan is also a review aid for environmental and energy management. The monitoring plan proforma worksheet is to be completed for each installation with LCP. At present it contains only administrative detail for MCP. Where there are plans to install and use any new MCP, you should engage with OPRED early. For existing MCP the proforma will be adapted in a future revision ahead of the compliance date(s) as reference in the regulations. LCP are individual combustion units equal to or greater than 50MWth (max rated input). MCP are boilers, heaters and dual fuel engines that are ≥1MWth and <50MWth (max rated input).
Reserved for Rev ID
Instructions to Operators
Please complete one copy of the worksheet "#1a LCP Blank Proforma" for your LCP. You must use an additonal sheet #1a if the permit has more than 4 x LCP. An example worksheet #1b is provided to help complete the proforma.
Please submit your completed worksheet #1a to OPRED via a PPC permit variation as an upload to PETS, by date TBC.
Please have your test personnel / service provider prepare a Site Specific Protocol (SSP) for each test campaign, under your monitoring plan. See below for link to MCERTS SSP guidance
Overview of this Template
Status: This template has been produced by OPRED as a monitoring plan proforma for Large Combustion Plant (LCP) for the calendar year 2022 and for the 3-year horizon 2022-2024. It is currently in draft form as part of gaining feedback and for use to draw up or check monitoring plans in 2022. The objective of the profoma is to provide standard data entry fields summarising an operator's monitoring plan for an installation with LCP so as to present consistent information to all stakeholders; operators, the regulator (OPRED), consultants & service providers (including MCERTS laboratories and test personnel). It is intended that the completed proforma should aid compliance with LCP conditions introduced into the offshore combustion installation PPC permits (as varied in August 2021 for the LCP BREF), in a consistent manner across all LCP permitted combustion plant.
Subject Matter: "Stack Emission Monitoring" is a general term used to describe a number of activities related to sampling, analysing, and reporting the emissions to air (of atmospheric pollutants) from the exhaust stacks of combustion plant in a variety of potential process environments. The emission monitoring activities described include: a) Preparation work prior to undertaking a stack emissions monitoring measurement campaign. Inputs to this include a Monitoring Plan (MP) and outputs include a Site Specific Protocol (SSP). b) Undertaking the site work associated with the operator's MP in accordance with the test campaign SSP and approved Standards. c) Calculating the Monitoring Results in accordance with the requirements of the MP and the SSP. d) Providing a final report for the client where in most cases the client is the process operator and/ or permit holder in line with regulatory requirements. e) Ensuring throughout that the workscope is in accordance with the client's requirements and the compliance requirements of any associated environmental permit.
The PPC Monitoring Plan :- Tab #1a proforma & #1b example
Description: The PPC Monitoring Plan is produced by the operator in connection with compliance with the PPC Permit for the installation. At any given time there must only be one live monitoring plan for each permitted installation. The MP should provide a summary worksheet for eligible LCP and (TBC) a worksheet for eligible Medium Combustion Plant (MCP). The MP proforma worksheet in this spreadsheet brings together key information from other documents in alignment with PPC permit monitoring conditions for LCP. The MP should be submitted as a permit variation to OPRED via the PETS portal. The monitoring plan should be provided to the Department by 30 September 2022, but operators are encouraged to upload sooner. The monitoring plan LCP worksheet contains the following sections as itemised in the proforma
Section A: Installation permit details
Section B: Installation operating details
Section C: LCP equipment design details consistent with A and B
Section D: LCP equipment operating details consistent with A, B and C
Section E: LCP equipment stack emission monitoring details including any permit ELV, sampling facilities, and dates of previous baseline testing
Section F: LCP monitoring including past, present, and future planned (expected) test campaigns - over the past 5 years and the next 3 years
The Site Review :- Operator to use their own proforma
Description: Once a monitoring plan for an installation is in place, a site review is recommended as a pre-cursor to any monitoring campaign. The site review is a visit conducted by the test organisation and test personnel or their representative, before undertaking stack emission monitoring measurements. The visit ensures that the physical and logistical situation associated with the installation and the test site is fully understood before the test team arrives on site to carry out the actual stack measurement work. The review focuses on the health and safety and practical considerations for testing, and how these relate to process operations and the process environment. The site visit will normally be undertaken several weeks or months before a campaign, and could typically last half a day. Importantly the site review interprets the operator's monitoring plan and provides essential information for determining the Site Specific Protocol (SSP) and for determining key inputs to the Risk Assessment (RA) process under offshore Integrated Safe Systems of Work (ISSOW) and associated permit-to-work requirements on the installation. Once a test location is well understood, repeat site review visits are usually not necessary between test campaigns. Existing PPC installations with a history of previous testing may therefore not require site review visits in any given year, unless test site conditions, test personnel, or other key aspects of the planned activity change significantly.
The Site Specific Protocol (SSP) :- Follow MCERTS guidance
Guidance: Detailed requirements of elements within a SSP can be found here: https://www.gov.uk/government/publications/mcerts-performance-standard-for-organisations-monitoring-manual-stack-emissions.
Purpose: The SSP is not a monitoring plan but is a site-specific guide to a stack emissions monitoring measurement campaign that is being scheduled to implement part of the objectives of a monitoring plan. The SSP is informed by the monitoring plan and the site review visit. There may be several versions of a SSP as a sub-set to a monitoring plan depending on when individual items of combustion plant equipment are to be tested, how they are to be tested, by whom, and to what detailed requirements and follow-up.
Description: The SSP is a document produced by the competent personnel scheduled to carry out a stack emission monitoring campaign to satisfy the operator's monitoring plan. The SSP is a requirement under the MCERTS personnel and equipment certification scheme and any associated Organisation's MCERTS accreditation scheme. A SSP is the measurement plan for each specific stack emission monitoring campaign. It covers the installation-specific application of a test organisation's technical procedures. The SSP describes how the measurement method is employed in a given situation. It should itemise the equipment and standards to be used.
Baseline Testing using SRM: For baseline stack emission monitoring to Standard Reference Methods (SRM) a comprehensive SSP is required in line with MCERTS for accredited Organisations carring out SRM testing for periodic monitoring purposes. The SSP should detail each of the pollutants being monitored using SRM and the specific BS EN standards being used. For example the SRM for NOx measurement is Chemiluminescence to BS EN 14792:2017 and for CO is Non-Dispersive Infrared Spectrometry (NDIR) to BS EN 15058:2017
Periodic Testing for Compliance Monitoring: For periodic stack emission monitoring for permit compliance purposes using SRM or Alternative Methods (AM) including Handheld Emissions Monitoring Systems (HEMS) that have MCERTS approval. A comprehensive SSP is required in line with MCERTS for use of HEMS as an AM for periodic monitoring purposes. NB. The AM method is an approved equivalent to a Standard Reference Method (SRM) by way of type approval tests to BS EN 14793:2017.
Guidance: Detailed requirements of elements within a SSP can be found at the government website here: https://www.gov.uk/government/publications/mcerts-performance-standard-for-organisations-monitoring-manual-stack-emissions. As a guide the following is a list of some of the key elements of a comprehensive SSP: a) The operator installation name and PPC permit details, and the operator contact details. b) The details of the specific monitoring campaign covered. Including name and accreditation / certification of organisation / personnel conducting testing, and planned date of tests. c) The overall monitoring objective(s) of the specific monitoring campaign in line with the monitoring plan. d) The objectives and techniques for measurement of specific pollutants; including frequency, ELV, reference conditions, SRM/AM standard, lab test procedures, uncertainty objectives. e) The operating characteristics and related parameters of the emission release point as relevant to the health and safety considerations and measurement techniques. f) The specific physical details including dimensions of the exhaust stack and the sampling point (sample port) on the stack. g) The details of test equipment calibration procedures including zero and span gases and impacts on sampling measurement uncertainties. h) A summary of any modifications required to technical procedures, deviation from standards, and associated justification reasons, together with any test objectives not being met. i) A summary of the data analysis, calculation, and reporting requirements of the test. j) An overall declaration relating to i) satisfactorily meeting the overall objectives, ii) operating information, iii) sample point location, and iv) details of monitoring. k) SSP sign-off by i) Test personnel and ii) Operator.
LCP Annual Monitoring Report proforma (2022 results)
Purpose: OPRED intend to provide an LCP annual monitoring report proforma to be used from the end of 2022 for reporting a summary of compliance monitoring results to OPRED in a consistent manner. The worksheet in this file has been intentionally left blank. No input required at this time. An update of requirements will be provided in the second half of 2022
End of Revision and Guidance Notes

## #1a LCP Blank Proforma
| PPC Monitoring Plan | Year: | 2022 | Revision:
By / Check:
Proforma - Annual Monitoring Plan Template for Large Combustion Plant - to be completed for each installation
A | Installation Permit Details: | Refer to PPC regulations for definition of LCP and MCP combustion plant
A1 | PPC Permit ID and Issue
A2 | Installation Name
A3 | Permit Holder Name (Company Name)
A4 | Operator Name (if different to permit holder)
A5 | Number of Large Combustion Plant (LCP)
A6 | Number of Medium Combsution Plant (MCP)
A7 | Number of other combustion plant >3MWth
B | Installation Operating Details: | Units | The details below should reflect your latest PPC Non Technical Summary (NTS) and / or BAT Review Report
B1 | Platform Electrical Demand - normal (MWe) | (MWe)
B2 | Platform Electrical Demand - maximum (MWe) | (MWe)
B3 | List of main electrical consumers (MWe) | (MWe)
B4 | List of Producing Fields including tie-backs | Text
B5 | Oil Export | Text
B6 | Gas Export | Text
B7 | Condensate Export | Text
B8 | Gas Re-injection / Gas Lift | Text
LCP equipment on permit - Details required to be provided to the Department under Monitoring Plan
Details are to be reviewed annually by Permit holder and aligned with PETS. NB. The permit holder should complete additional sheets if the Installation has >4 LCP units
|  |  | LCP #1 | LCP #2 | LCP #3 | LCP #4
C | LCP Equipment Design Details: | Units | NB. The parameters below should match your latest PPC permit revision
C1 | PPC Permit Item Number | No.
C2 | Original Equipment Manufacturer (OEM) | Text
C3 | Equipment Make and Model | Text
C4 | Equipment Make and Model (alternative) | Text
C5 | Main Fuel Type (Gas / Diesel / Dual Fuel) | Text
C6 | Backup Fuel Type (Gas / Diesel / Dual Fuel) | Text
C7 | Plant Tag ID Number | Text
C8 | Type of Combustion Plant | Text
C9 | Primary Purpose | Text
C10 | Maximum Rated Output (MW) | (MW)
C11 | Maximum Thermal Input (MWth) | (MWth)
C12 | Thermal Efficiency at Max. Rating (%) | (%)
C13 | Combustion Type (SAC / DLE / Other) | Text
C14 | Date Commissioned if since Aug 2017 | Date
C14 | Is decommissioning likely in the next 3 years? | Yes/No
D | LCP Equipment Operating Details: | Units | NB. The parameters listed below should match your typical operating duty and hours should match EEMS records
D1 | Description of Duty | Text
D2 | Normal Operating Load (MW) | MWe
D3 | Normal Operating Duty (1-oo-2 etc) | Text
D4 | Actual Hours run last calendar year | Hrs/yr
D5 | Of which run hours on diesel fuel | Hrs/yr
D6 | Expected Hours run this calendar year | Hrs/yr
D7 | Do you monitor plant Load (in MW) and how? | Text
D8 | Is the plant fitted with Heat Recovery (WHRU)? | Yes/No
E | LCP Equipment Monitoring Details: | Units | NB. The parameters listed below should match your PPC permit and installation PPC testing history
E1 | Normal Operating Load % of Rating (calculated) | % | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
E2 | What is the permitted NOx ELV for the LCP? | mg/Nm3
E3 | Does the LCP have a NOx BAT derogation? | Yes/No
E4 | Has the plant been baseline tested for NOx and CO emissions using SRM to MCERTS standards? | Yes/No
E5 | Date when plant was last tested for NOx and CO using SRM equipment & MCERTS test standards | Date
E6 | Is the relevant test report uploaded in PETS? | Yes/No
E7 | Does the exhaust stack have sampling ports? | Yes/No
E8 | What is the size of the ports (if known)? | Size
E9 | Is temporary platform access (e.g. scaffolding) needed to access the ports safely? | Text
E10 | Has unit been baseline tested for Unburnt Hydrocarbons (Methane and non-Methane) using SRM to MCERTS? | Text
E11 | Has unit been baseline tested for SO2 using SRM to MCERTS or is fuel low H2S / low sulphur? | Text
E12 | Do you undertake regular Fuel Gas sampling (e.g. as part of your ETS MMP requirements) | Yes/No
F | LCP Stack Monitoring Summary: | Units | NB. The parameters below should match Operator current intentions for the next 1-3 years. These are not 'fixed' and can be amended through ongoing discussion and annual review with the Department
F1 | What monitoring/testing has been carried out in the last 5 calendar years? Was this to SRM or AM or Other? | Text
F2 | What monitoring/testing is planned for the current 'Y' calendar year? Is this to SRM or AM or Other? | Year?
F3 | What monitoring/testing is planned for the Y+1 calendar year? Is this to SRM or AM or Other? | Year+1?
F4 | What monitoring/testing is planned for the Y+2 calendar year? Is this to SRM or AM or Other? | Year+2?
F5 | Are you intending to trial Predicitive Emissions Monitoring (PEMS) in the next 1-3 years with a view to using it as part of compliance monitoring and/or routine monitoring? [Optional] | Text (Optional)
F6 | Are you intending to train and qualify your own personnel in the next 1-3 years for operating AM test equipment to MCERTS? [Optional] | Text (Optional)
Requirements: All gold cells of this template are to be completed by operator for 2022 and returned to OPRED via PETS. See illustrative example sheet
The Monitoring Plan does not constitute an MCERTS Site Specific Protocol (SSP). You will be required to draw up a SSP separately for each MCERTS stack testing campaign
Once OPRED is in receipt of your 2022-2024 Monitoring Plan and any campaign-specific SSP these will be reviewed and further information may be requested by OPRED
Refer to UK Government website for SSP considerations https://www.gov.uk/guidance/monitoring-stack-emissions-technical-guidance-for-selecting-a-monitoring-approach

## #1b LCP Example Proforma
| PPC Monitoring Plan | Year: | 2022 | Revision: | 0.2 | 2022-02-15
|  |  |  | By / Check: | SL (OPRED) | DM (OPRED)
Example Proforma - Annual Monitoring Plan Template for Large Combustion Plant
A | Installation Permit Details: | Refer to PPC regulations for definition of LCP and MCP combustion plant
A1 | PPC Permit ID and Issue | PPC/125/6
A2 | Installation Name | Albatross Bravo
A3 | Permit Holder Name (Company Name) | OPRED Example Template North Sea Limited
A4 | Operator Name (if different to permit holder) | n/a
A5 | Number of Large Combustion Plant (LCP) | 4
A6 | Number of Medium Combsution Plant (MCP) | 0
A7 | Number of other combustion plant >3MWth | 3
B | Installation Operating Details: | Units | The details below should reflect your latest PPC Non Technical Summary (NTS) and / or BAT Review Report
B1 | Platform Electrical Demand - normal (MWe) | (MWe) | 46
B2 | Platform Electrical Demand - maximum (MWe) | (MWe) | 48
B3 | List of main electrical consumers (MWe) | (MWe) | LP and MP Compressors (12MWe), 3 x WIP (15MWe), 2 x Oil Transfer Pumps (3MWe), 3 x SWRI Pumps (6MWe)
B4 | List of Producing Fields including tie-backs | Text | Albatross North, Albatross South, Ptarmigan, Swallow
B5 | Oil Export | Text | Yes, via Shuttle Tanker
B6 | Gas Export | Text | Yes, via CATS pipeline to Teeside
B7 | Condensate Export | Text | n/a
B8 | Gas Re-injection / Gas Lift | Text | No Gas Lift. Gas Re-injection ceased in 2018 and gas export commenced in 2019
LCP equipment on permit - Details required to be provided to the Department under Monitoring Plan
Details are to be reviewed annually by Permit holder and aligned with PETS. NB. The permit holder should complete additional sheets if the Installation has >4 LCP units
|  |  | LCP #1 | LCP #2 | LCP #3 | LCP #4
C | LCP Equipment Design Details: | Units | NB. The parameters below should match your latest PPC permit revision
C1 | PPC Permit Item Number | No. | 1 | 2 | 5 | 11
C2 | Original Equipment Manufacturer (OEM) | Text | GE / Baker Hughes | GE / Baker Hughes | Siemens | Hamworthy
C3 | Equipment Make and Model | Text | LM2500+G4 | LM2500+G4 | SGT-400 | MAL80BF
C4 | Equipment Make and Model (alternative) | Text | PGT25+G4 | PGT25+G4 | Alstom Cyclone | n/a
C5 | Main Fuel Type (Gas / Diesel / Dual Fuel) | Text | Gas | Gas | Gas | Gas
C6 | Backup Fuel Type (Gas / Diesel / Dual Fuel) | Text | Diesel | Diesel | n/a | Diesel
C7 | Plant Tag ID Number | Text | PP-MDC-6001A | PP-MDC-6001B | PP-K-201 | ZXF-4201
C8 | Type of Combustion Plant | Text | Gas Turbine | Gas Turbine | Gas Turbine | Steam Boiler
C9 | Primary Purpose | Text | Power Generation | Power Generation | Gas Compression driver | Process Heating
C10 | Maximum Rated Output (MW) | (MW) | 31.9 | 31.9 | 12.9 | 49.6
C11 | Maximum Thermal Input (MWth) | (MWth) | 85.8 | 85.8 | 38.8 | 51.1
C12 | Thermal Efficiency at Max. Rating (%) | (%) | 37.1 | 37.1 | 33.2 | 90
C13 | Combustion Type (SAC / DLE / Other) | Text | SAC | SAC | DLE | Low Nox Burners
C14 | Date Commissioned if since Aug 2017 | Date | n/a | n/a | 2019-03-01 | n/a
C14 | Is decommissioning likely in the next 3 years? | Yes/No | No | No | No | No
D | LCP Equipment Operating Details: | Units | NB. The parameters listed below should match your typical operating duty and hours should match EEMS records
D1 | Description of Duty | Text | Main Power Generation | Main Power Generation | Export Gas Compressor | Process Heating & COTS
D2 | Normal Operating Load (MW) | MWe | 23 | 23 | 11.5 | 38
D3 | Normal Operating Duty (1-oo-2 etc) | Text | 2-oo-2 | 2-oo-2 | 1 x 100% | 1 x 100%
D4 | Actual Hours run last calendar year | Hrs/yr | 7124 | 7268 | 6925 | 6724
D5 | Of which run hours on diesel fuel | Hrs/yr | 223 | 122 | n/a | 305
D6 | Expected Hours run this calendar year | Hrs/yr | 7500 | 7500 | 6800 | 6200
D7 | Do you monitor plant Load (in MW) and how? | Text | Yes (off Generator) | Yes (off Generator) | Yes (via Torquemeter) | No (fuel valve % opening only)
D8 | Is the plant fitted with Heat Recovery (WHRU)? | Yes/No | Yes | Yes | No | No
E | LCP Equipment Monitoring Details: | Units | NB. The parameters listed below should match your PPC permit and installation PPC testing history
E1 | Normal Operating Load % of Rating (calculated) | % | 72.1% | 72.1% | 89.15% | 76.61%
E2 | What is the permitted NOx ELV for the LCP? | mg/Nm3 | 480 | 480 | 350 | 100
E3 | Does the LCP have a NOx BAT derogation? | Yes/No | Yes | Yes | No | No
E4 | Has the plant been baseline tested for NOx and CO emissions using SRM to MCERTS standards? | Yes/No | Yes | Yes | No | Yes
E5 | Date when plant was last tested for NOx and CO using SRM equipment & MCERTS test standards | Date | 2016-09-01 | 2016-09-01 | n/a | 2016-09-01
E6 | Is the relevant test report uploaded in PETS? | Yes/No | Yes | Yes | n/a | Yes
E7 | Does the exhaust stack have sampling ports? | Yes/No | Yes | Yes | No | Yes
E8 | What is the size of the ports (if known)? | Size | 2" flanged | 2" flanged | n/a (2" specified) | 4" flanged
E9 | Is temporary platform access (e.g. scaffolding) needed to access the ports safely? | Text | No , ports are accessible from existing permanent walkway. | No , ports are accessible from existing permanent walkway. | No, 2 ports are to be installed in a accessible location | Yes, a small scaffold platform is required for safe access
E10 | Has unit been baseline tested for Unburnt Hydrocarbons (Methane and non-Methane) using SRM to MCERTS? | Text | Yes (2016) | Yes (2016) | No | No
E11 | Has unit been baseline tested for SO2 using SRM to MCERTS or is fuel low H2S / low sulphur? | Text | Tested in 2016. Gas fuel has low H2S. Desel is Low-sulphur | Tested in 2016. Gas fuel has low H2S. Desel is Low-sulphur | Not tested, but gas and diesel are low sulphur | Not tested, but gas and diesel are low sulphur
E12 | Do you undertake regular Fuel Gas sampling (e.g. as part of your ETS MMP requirements) | Yes/No | Yes (export gas) | Yes (export gas) | Yes (export gas) | Yes (export gas)
F | LCP Stack Monitoring Summary | Units | NB. The parameters below should match Operator current intentions for the next 1-3 years. These are not 'fixed' and can be amended through ongoing discussion and annual review with the Department
F1 | What monitoring/testing has been carried out in the last 5 calendar years? Was this to SRM or AM or Other? | Text | None since SRM in 2016 | None since SRM in 2016 | None (no ports fitted yet) | Routine Boiler checks using AM portable unit (with some exceptions to MCERTS std)
F2 | What monitoring/testing is planned for the current 'Y' calendar year? Is this to SRM or AM or Other? | 2022 | MCERTS using AM of NOx, CO, SO2, ( plus O2, CO2). No UHC / CH4 | MCERTS using AM of NOx, CO, SO2, ( plus O2, CO2). No UHC / CH4 | None, but sample ports are planned to be fitted in the 2022 TAR | MCERTS using AM of NOx, CO, SO2, ( plus O2, CO2). No UHC / CH4
F3 | What monitoring/testing is planned for the Y+1 calendar year? Is this to SRM or AM or Other? | 2023 | MCERTS using SRM and onshore UKAS Lab | MCERTS using SRM and onshore UKAS Lab | MCERTS using SRM and onshore UKAS Lab | MCERTS using SRM and onshore UKAS Lab
F4 | What monitoring/testing is planned for the Y+2 calendar year? Is this to SRM or AM or Other? | 2024 | To be advised in 2023 based on 2022 & 2023 | To be advised in 2023 based on 2022 & 2023 | To be advised in 2023 based on 2022 & 2023 | To be advised in 2023 based on 2022 & 2023
F5 | Are you intending to trial Predicitive Emissions Monitoring (PEMS) in the next 1-3 years with a view to using it as part of compliance monitoring and/or routine monitoring? [Optional] | Text (Optional) | Yes, we plan to trial PEMS for all our LCP units and for some of our other non-LCP units (miscellaneous combustion plant). We plan to participate in the OEUK ATG PEMS Working Group when it starts up in 2022.
F6 | Are you intending to train and qualify your own personnel in the next 1-3 years for operating AM test equipment to MCERTS? [Optional] | Text (Optional)
Requirements: All gold cells of this template are to be completed by operator for 2022 and returned to OPRED via PETS. Text shown is illustrative example only.
The Monitoring Plan does not constitute an MCERTS Site Specific Protocol (SSP). You will be required to draw up a SSP separately for each MCERTS stack testing campaign
Once OPRED is in receipt of your 2022-2024 Monitoring Plan and any campaign-specific SSP these will be reviewed and further information may be requested by OPRED
Refer to the webpage for SSP considerations https://www.gov.uk/guidance/monitoring-stack-emissions-technical-guidance-for-selecting-a-monitoring-approach

## #2 LCP Monitoring Report 2022
Page is intentially left blank - no input required at this time
OPRED will update this page to include a emissions monitoring data report proforma.
This will provide a consistent format (summary report) for reporting annual emissions monitoring data for compliance purposes (following the end of each calendar year)
The report proforma will be used for reporting the results of PPC permit compliance tests from the end of 2022.