Technical Standard - Design, Inspection, Maintenance and Testing of Ancillary Fuel Installations

Version 1 – October 2022
1
ESTATE MANAGEMENT
TS2022-08 Petroleum - 05
Document Information
DIO Sponsor: / Andrew Parker MCIWEM, C.WEM, / MAPM	Date of Issue: 31/10/2022
Contact if different from above Sponsor: / Matthew Spare BEng MSc CEng MIMechE / Principal Mechanical Engineer (Mechanical and Fuel Infrastructure) / Technical Services / Defence Infrastructure Organisation / St George’s House / Defence Infrastructure Organisation Head Office / DMS Whittington / Lichfield / Staffordshire / WS14 9PY
Mob: 07866143508 │Email: matthew.spare101@mod.gov.uk │Website:
https://www.gov.uk/government/organisations/defence-infrastructure-organisation
Who should read this: DIO Staff and Contractors; Public, Private Partnerships, Private Finance Initiatives Project Managers/Commercial Officers, Commanding Officers / Heads of Establishment (CO/HoEs) and representatives; and Chief Environment and Safety Officers (CESOs) or equivalent, Estate Facilities Managers (EFMs), Senior Estate Facilities Managers (SEFMs), Authorising Engineers (Petroleum), Authorised Persons (Petroleum) (AP), Maintenance Management Organisations (MMOs) and TS-Pet-03 Professional Inspectors.
When it takes effect: Immediately	When it is due to expire: When rescinded
Equality and Diversity Impact Assessment / This policy has been Equality and Diversity Impact Assessed in accordance with the Department’s / Equality and Diversity Impact Assessment Tool against: / Part 1 Assessment Only (no diversity impact found)

Document Name:	Design, Inspection, Maintenance and Testing of Ancillary Fuel Installations
Version No:	1.0
Version Date:	October 2022
Author:	Geoffrey Ward Asset Class Engineer (Fuels)
Reviewed by:	Matthew Spare Principal Mechanical Engineer
Review Date:	27/10/2022

2
Date Issued	Version	Author	Reason for Change
27/10/2022	1.0	Geoffrey Ward	New Document

FOREWORD
This Technical Standard, hereafter known as ‘this Standard’, is published by Defence Infrastructure Organisation (DIO) for application across all areas of the Ministry of Defence (MOD). This Standard mandated for all new contracts including USVF, overseas and Private Finance Initiative (PFI) arrangements. For existing contracts, no work involving expenditure on any MOD account is to be entered into without prior authority from the appropriate MOD officer for that location or facility. The term, Maintenance Management Organisation (MMO) is used throughout this Standard to describe the organisation responsible for undertaking the procurement, operation, and maintenance of Ancillary Fuel Installations (AFI) on an MOD site – the term is equally applicable to establishments where more extensive service partnership arrangements exist.
DOCUMENT SYNOPSIS
This Standard defines the requirements for the planning, design, installation, commissioning and decommissioning of all new MOD AFI. This Standard gives the required guidance on the selection of equipment necessary for the safe storage of fuels. The technical content of this Standard is sourced from the various British Standards and existing MOD best practice. NOTE! This Standard specifically excludes installations that store Class I petroleum products such as Petrol/Gasoline, for these installations consult DIO Technical Standards – Petroleum – 01 or 04.
This Standard is not, however, a technical guide to the practical aspects of maintenance, inspection and testing of AFI and associated equipment, which is left to the professional skills and judgement of Competent Person(s) undertaking the work.
DOCUMENT HISTORY

3

CONTENTS
FOREWORD / DOCUMENT SYNOPSIS			3 / 3
1.		INTRODUCTION	6
	1.1	AIM	6
	1.2	SCOPE AND LIMITATIONS	6
	1.3	SAFETY	8
	1.4	STANDARDS AND REGULATIONS	8
	1.5	ABBREVIATIONS	13
	1.6	DEFINITIONS	14
2.		APPLICATION OF THIS STANDARD ELSEWHERE	16
	2.1	USVF BASES	16
	2.2	OVERSEAS ESTATES	16
3.		PLANNING	18
	3.1	STATEMENT OF REQUIREMENT	18
	3.2	INITIAL PLANNING	18
	3.3	SITING BOARD	19
	3.4	RISK ASSESSMENT - GENERAL	19
	3.5	RISK ASSESSMENT - FIRE	20
	3.6	RISK ASSESSMENT - ENVIRONMENTAL	20
	3.7	RISK ASSESSMENT - CONSTRUCTION	21
	3.8	RISK ASSESSMENT - DANGEROUS SUBSTANCES EXPLOSIVE ATMOSPHERE REGULATIONS (DSEAR)	21
4.		DESIGN REQUIREMENTS	23
	4.1	GENERAL DESIGN REQUIREMENTS	23
	4.2	INITIAL DESIGN (CONCEPT DESIGN)	23
	4.3	DETAIL DESIGN REQUIREMENTS FOR TANKS	24
	4.4	TANK & PIPEWORK PAINTING AND COATING	27
	4.5	DETAIL DESIGN REQUIREMENTS FOR TANK VENT PIPES	28
	4.6	DETAIL DESIGN REQUIREMENTS FOR TANK FOUNDATION AND BUND	28
	4.7	DETAIL DESIGN REQUIREMENTS ROAD TANKER DELIVERY STAND	29
	4.8	DETAIL DESIGN REQUIREMENTS FILL POINTS	29
	4.9	DETAIL DESIGN REQUIREMENTS FOR PIPEWORK	29
	4.10	DETAIL DESIGN REQUIREMENTS FOR PUMP SYSTEMS	31
	4.11	DETAIL DESIGN REQUIREMENTS FOR POLISHING SYSTEMS	31
	4.12	DETAIL DESIGN REQUIREMENTS FOR CLASSIFICATION AND CONTROL OF A HAZARDOUS AREA	32
	4.13	DETAIL DESIGN REQUIREMENTS FOR DRAINAGE SYSTEM	32
	4.14	DETAIL DESIGN REQUIREMENTS FOR MECHANICAL & ELECTRICAL DUCTS.	33
	4.15	DETAIL DESIGN REQUIREMENTS FOR FIRE FIGHTING EQUIPMENT	33
	4.16	DETAIL DESIGN REQUIREMENTS FOR WARNING AND H&S NOTICES	33
	4.17	DETAIL DESIGN REQUIREMENTS FOR LEVEL MEASUREMENT & CONTENTS GAUGES	33
	4.18	DETAIL DESIGN REQUIREMENTS FOR ALARMS AND CONTROLS	35
5.		WORKING PLATFORMS, STAIRWAYS AND ACCESS LADDER	35
6.		LABELLING AND MARKING	35
	6.1	TANK AND PIPEWORK	36
7.		REQUIREMENTS FOR LEAK DETECTION AND CONTAINMENT	38
	7.1	GENERAL	38

4

7.2	SYSTEM CLASS	38
7.3	LEAK CONTAINMENT	38
7.4	LEAK DETECTION	39
REQUIREMENTS FOR ELECTRICAL EQUIPMENT	39
8.1	GENERAL	39
8.2	HAZARDOUS AREA CLASSIFICATION	39
8.3	SELECTION AND INSTALLATION OF ELECTRICAL EQUIPMENT	39
8.4	LOCATION OF ELECTRICAL EQUIPMENT	40
8.5	ELECTRICAL ISOLATION AND SWITCHING	40
8.6	MAIN SWITCHGEAR	40
8.7	ELECTRICAL OVERCURRENT PROTECTION	41
8.8	PROTECTION AGAINST STATIC ELECTRICITY	41
8.9	PROTECTION AGAINST ELECTRIC SHOCK	42
8.10	ELECTRICAL EARTHING	42
8.11	CONDUIT, DUCTING, PIPES AND TRUNKING	42
8.12	BONDING FOR ELECTRIC SHOCK AND EXPLOSION PROTECTION	43
8.13	INTERCONNECTION OF EARTHING SYSTEMS	43
8.14	ELECTRICAL WIRING SYSTEMS	43
8.15	ELECTRICAL LABELS AND WARNING NOTICES	43
8.16	ELECTRICAL INSPECTION AND TESTING	44
DESIGN APPROVALS	44
9.1	A DESIGN APPROVALS PROCESS	44
CONSTRUCTION	44
10.1	GENERAL	44
TESTING, COMMISSIONING AND ACCEPTANCE	45
11.1	CERTIFICATE OF FITNESS FOR PURPOSE	45
11.2	TESTING	45
11.3	VERIFICATION HAZARDOUS AREAS	45
11.4	COMMISSIONING	46
11.5	HANDOVER	47
DECOMMISSIONING	48
12.1	GENERAL	48
12.2	TANK DECOMMISSIONING	49
12.3 ABOVEGROUND TANKS	50
12.4	BURIED TANKS	50
12.5	PIPEWORK	50
12.6	OWI AND DRAINAGE	51
12.7	ELECTRICAL INSTALLATION	51
PERIODIC INSPECTION AND MAINTENANCE SCHEDULES AND FREQUENCIES	51
13.1	GENERAL	51
13.2	FUEL QUALITY	51
13.3	REPAIRS AND MODIFICATIONS	53
13.4	PERIODIC INSPECTION AND MAINTENANCE SCHEDULES FOR AFI	54
TECHNICAL AUTHORITY	56
14.1	GENERAL	56
5

1.	Introduction
1.1	Aim
1.1.1 The aim of this Standard is to provide guidance and direction on the design, construction, repair, maintenance, testing, commissioning and decommissioning requirements of AFI on MOD Establishments. These would normally store fuel for Boilers, Generators, Fire Pumps, Waste Petroleum Products and similar products within MOD establishments. This Standard provides guidance on tank design types, as well as the required planning, health and safety implications of both installation and decommissioning.
1.1.2 This Standard aims to reference the guidance and requirements of relevant legislation, British Standards, Codes of Practice, MOD policy and standards pertaining to the design, repair, maintenance and the decommissioning of MOD AFI with the purpose of:
- Enabling the MOD to comply with the requirements of the relevant Legislation, British Standards and UK Regulatory Requirements,
- Promoting a common and consistent approach to the design, repair, maintenance, testing, commissioning and decommissioning of AFI throughout the MOD’s estate (both UK and overseas),
- Assisting the Designer and installer of new facilities and the modifier and maintainer of existing facilities, in the precautions necessary to ensure that installations are fit for use,
- Enabling the production of a maintenance regime.
1.1.3 It is not the intention that this Standard be a single source of information, but to refer the reader, where necessary, to the relevant external industry publications. It is therefore expected that whilst this Standard contains technical guidance, the reader should have access to the other industry publications referred to within section 1.4.
1.1.4 The SFG20 Maintenance Schedule referred to within this Standard should be adhered to in order to assist in ensuring that MOD AFI are maintained in accordance with statutory and client requirements for:
- Safety of operation,
- Environmental protection,
- Equipment reliability and longevity.
1.2	Scope and Limitations
1.2.1 This Standard is applicable to all existing, new and refurbished MOD AFI and associated equipment including:
- Tanks for the storage of Class III & ‘kerosene-based products’, including secondary containment, vents, fill points, inspection hatches and manways, working platforms and access ladders.
- All pipework, above ground or buried, associated with the transfer of these fuel products,
- All electrical equipment including cabling, wiring, bonding, alarms and level monitoring, lighting, electrical distribution and lightning protection systems,
- Civil ground works including tank foundation,
- Drainage including type of drainage system, buried Oil Water Interceptors (OWIs), pipework and connections with local drainage where applicable where not covered by MOD Project Aquatrine,
- Physical protection of the AFI.
It is not the intention that retrospective design and construction work is undertaken at existing facilities as a means of complying with the guidance in this Standard. Existing
6

facilities should however follow this Standard where the guidance relates to maintenance, decommissioning or where there are planned modification works to the installation.
1.2.2 Additional to the equipment requirements, the following forms part of the scope of this Standard:
- Design and planning of the installation including location, layout, and spatial requirements,
- Overview of risk assessments requirements to assist in mitigation of foreseen hazards relating to the operation and maintenance of the facility as well as any hazards impacting the environment,
- Overview of hazardous area classification requirements for identification of potential flammable and explosive zones,
- Testing and commissioning on completion of construction,
- Procedural guidance on the decommissioning of existing installations including isolation of services, making safe equipment left in-situ, and removal of equipment and hazardous waste from site.
1.2.3 This Standard does not apply to the following:
- Fabrication of specific equipment. It is assumed for the purposes of this Standard that the equipment installed shall be supplied by a reputable manufacturer to relevant British Standards and industry codes of practice,
- Specific guidance on the creation of risk assessments. Detailed guidance found within JSP 375 Preliminary Documents should be followed for the undertaking of risk assessments on the MOD estate,
- Specific guidance on production of hazardous area classification. Detailed guidance on hazardous area classification is found within JSP 375 Volume 1 Chapter 9, Practitioner Guide 2018/02 High Flashpoint Class III Fuels – DSEAR, BS EN 60079-10-1 and EI 15.
- The provision of any fixed firefighting equipment in close proximity to the installation forming part of the site wide firefighting infrastructure, see Defence Infrastructure Fire Standards (DIFS) for clarification,
- Pipework, equipment or appliances downstream of the customer buried drainage and OWI where fitted,
- Electrical supply upstream of the distribution panel supplying the AFI. NOTE! For installations where a hazardous area is present the earthing of the electrical supply must be of the TN-S or TT type.
1.2.4 For AFI located at domestic dwellings the construction and installation of tanks of 3500 litres or less is covered by Building Regulations as per Approved Document ‘J’ Combustion appliances and fuel storage systems.
- Tanks and fuel supply systems should be designed, constructed, installed and maintained in line with the requirements of BS5410:1 Code of practice for liquid fuel firing Part 1: Installations for space heating and hot water supply purposes for domestic buildings.
- Building Standards are controlled on the UK MoD occupied Estate by the DIO Building Control Compliance Authority, Group Mailbox DIOTS-BEHS-worksnotification@mod.gov.uk
- NOTE! Because Devolved governments are responsible for the Implementation of Building Standards in their own administrations MOD DIO Building Standards control processes may vary by location.
- This document offers no further guidance on tanks of 3500 litres or less at domestic dwellings. Should there be any question of the applicability of this requirement at domestic dwellings DIO Technical Services (TS) should be consulted.
7

1.3	Safety
1.3.1 All work is to be undertaken in accordance with the JSP 317 Part 2 - Guidance Volumes 1 to 4, JSP 375 Volume 3 Chapter 5 – Petroleum Installation, JSP 375 Volume 3 Chapter 3 – Electrical and JSP 418 – Management of Environmental Protections in Defence Part 1 - Directive.
1.3.2 The line manager of the Fuels and Lubricants section, hereby known as the Operating Authority (OA), has delegated authority from the Head of Establishment (HoE) for the installations. Although not clearly specific to AFI the current version of JSP 317 can be used for guidance for the setting up and administering of appointments. Authority must be given by the OA before any works can be undertaken on a Petroleum Installation.
1.3.3 The MMO will ensure the ‘Competence’ of all staff responsible for the implementation of this Standard, they will also have a system in place to demonstrate that ‘Competence’.
1.3.4 The Authorised Person (Petroleum) (AP) is responsible for the practical implementation and application of JSP 375 Volume 3 Chapter 5 on AFI.
1.4	Standards and Regulations
All work shall comply with the latest editions of appropriate standards not only but including: British Standards:
BS EN 124 Part 1	Gully tops and manhole tops for vehicular and pedestrian areas. Definitions, classification, general principles of design, performance requirements and test methods
BS EN 752	Drain and sewer systems outside buildings - sewer system management
BS 799 Part 5	Oil Burning Equipment. Carbon Steel Oil Storage Tanks. Specification
BS EN 858 Part 1	Separator Systems for Light Liquids (e.g. Oil and Petrol)
BS EN 858 Part 2	Separator Systems for Light Liquids (e.g. Oil and Petrol)
BS EN 1610	Construction and testing of drains and sewers
BS EN 1992-1- / 1:2004+A1:2014 Eurocode 2:	Design of concrete structures.
BS ISO 4406:2021	Hydraulic fluid power - Fluids - Method for coding the level of contamination by solid particles.
BS 5410-1	Code of Practice for liquid fuel firing Part 1: Installations for space heating and hot water supply purposes for domestic buildings.
BS 5410-2	Code of Practice for liquid fuel firing Part 2: Installations providing space heating, hot water and steam supply services to non-domestic buildings.
BS 5410-3	Code of practice for oil firing Part 3: Installations for furnaces, kilns, ovens, oil-fuelled standby generators and other industrial purposes.
BS 6187	Code of practice for full and partial demolition
BS 7430	Code of practice for protective earthing of electrical installations.

8

BS 7671	Requirements for Electrical Installations. IET Wiring Regulations
BS 8500:2019	Concrete – Complementary British Standard to BS EN 206.
BS 10175	Investigation of potentially contaminated sites Code of practice
BS EN 12285 Part 1	Workshop Fabricated Steel Tanks (Underground)
BS EN 12285 Part 2	Workshop Fabricated Steel Tanks (Aboveground)
BS EN 12285 Part 3	Workshop fabricated steel tanks — Part 3: Horizontal cylindrical single skin and double skin tanks for the underground storage of flammable and nonflammable water polluting liquids for heating and cooling of buildings.
BS EN 13160 Parts 1-7	Leak Detection Systems.
BS EN 13616-1	Overfill prevention devices for static tanks for liquid fuels – Overfill prevention devices with closure device
BS EN ISO 14122 Parts 1-4	Safety of machinery – Permanent means of access to machinery
BS EN 14125	Thermoplastic and Flexible Metal Pipework for Underground Installation at Petrol Filling Stations.
BS EN ISO 16852:2016	Flame arresters – Performance requirements, test methods and limits for use
BS EN ISO 28300:2008	Petroleum, petrochemical and natural gas industries – Venting of atmospheric and low-pressure storage tanks
BS EN 60079-10-1	Explosive atmospheres – Part 10-1: Classification of areas - Explosive gas atmospheres
BS EN 60079-14	Explosive Atmospheres – Part 14: Electrical Installations Design Selection and Erection
BS EN 60079-15	Explosive atmospheres — Part 15: Equipment protection by type of protection “n”
BS EN 60079-17	Explosive Atmospheres - Part 17: Electrical installations inspection and maintenance
BS EN 60079-25	Explosive Atmospheres Part 25: Intrinsically safe electrical systems
BS EN 60079-26	Explosive Atmospheres Part 26: Equipment with Equipment Protection Level (EPL) Ga
BS EN 60079-30-1	Explosive atmospheres — Part 30-1: Electrical resistance trace heating — General and testing requirements
BS EN 60079-30-2	Explosive atmospheres — Part 30-2: Electrical resistance trace heating — Application guide for design, installation and maintenance
BS EN 60529:1992+A2:2013	Degrees of protection provided by enclosures (IP Code).
BS EN 61558-2-6	Safety of transformers, reactors, power supply units and similar products for supply voltages up to 1100 V.
BS EN 62305-3	Protection against lightning Part 3: Physical damage to structures and life hazard

MOD Standards:
JSP 317 Part 1 & Part 2	Joint Service Safety Regulations for the Storage of Fuels and Lubricants. Web address -

9

	https://www.gov.uk/government/publications/jsp-317-joint-
	service-safety-regulatio ns-fo r-the-joint-storage-and-handling-of-
	fuels-lubricants-f-l
JSP 375	Joint Service Health and Safety Handbook. Web address - https://www.gov.uk/government/collections/jsp-375-health-and-
	safety-handbook
JSP 418	Management of Environmental Protection in Defence. Web address - https://www.gov.uk/government/publications/jsp-418-
	mod-corporate-environmental-protection-manual
JSP 850	Infrastructure and Estate Policy. Web address - https://www.gov.uk/guidance/knowledge-in-defence-kid

PG 03/09	Low Voltage Electrical Installations on MOD Property. Practitioner Guide 03/09. Web address see mid page 2009 - https://www.gov.uk/government/publications/practitioner-guides-
	2017
PG 2017/02	The Inspection, Testing, and Certification of Low Voltage Electrical Installations on the Defence Estate. Web address - https://www.gov.uk/government/publications/practitioner-guides-
	2017
PG 2018/02	High Flashpoint Class III Fuels – DSEAR (Dangerous Substances and Explosive Atmosphere Regulations). Web address - https://www.gov.uk/government/publications/practitioner-guides-
	2018

DIFS	Defence Infrastructure Fire Standards. Web address - https://www.gov.uk/government/publications/defence-
	infrastructure-fire-standards

Technical Standard – Petroleum – 01	Specialist Works on Petroleum Installations on MOD Property. Web address - https://www.gov.uk/government/publications/dio-
	technical-guidance-documents
Technical Standard – Petroleum - 02	Inspection, Maintenance and Testing of Equipment Installed at Petroleum Installations on MOD Property. Web address - https://www.gov.uk/government/publications/dio-technical-
	guidance-documents

Technical Standard – Petroleum - 03	Professional Inspection of Fuel Infrastructure and Flammable Dangerous Goods Stores. Web address - https://www.gov.uk/government/publications/dio-technical-
	guidance-documents
Technical Standard – Petroleum – 04	Design, Inspection, Maintenance and Testing of Equipment Installed at MOD Mechanical Transport Filling Installations (MTFIs). Web address - https://www.gov.uk/government/publications/dio-technical-
	guidance-documents
DSA 02	Defence land safety regulator policy and regulations for health, safety and environmental protection. Web address - https://www.gov.uk/government/publications/land-system-
	safety-and-environmental-protection-regulations
DSA 03 DLSR	Fuel and gas safety and environmental regulations: defence code of practice (DCOP). Web address -

10

	https://www.gov.uk/government/publications/land-system-
	safety-and-environmental-protection-regulations
SA 2021/02	Safety Alert SA 2021/02 Generator Firewire Failure. Web address - https://www.gov.uk/government/publications/safety-
	alerts-2021

Health and Safety Executive (HSE)
HSG 176	Storage of Flammable Liquids in Tanks
CDM	Managing health and safety in construction – Construction (Design and Management) Regulations 2015 – Guidance on Regulations – L153
L138 DSEAR	Dangerous Substances and Explosive Atmospheres Regulations 2002. Approved Code of Practice and guidance
INDG370	Controlling Fire and Explosion Risks in the Workplace. / A Brief Guide to the Dangerous Substances and Explosive / Atmospheres Regulations
HSE GS4	Guidance Note GS4 (Fourth edition) Safety requirements for pressure testing.

Energy Institute Publications
APEA/EI – The Blue Book	Design Construction Modification Maintenance & Decommissioning of Filling Stations
EI – MCoSP Part 1	Model code of safe practice Part 1:The selection, installation, inspection and maintenance of electrical and non-electrical apparatus in hazardous areas
EI 15	EI Model code of safe practice – Part 15 – Area classification for installations handling flammable fluids – 4th edition.
EI -	Guidelines on earthing/grounding/bonding in the oil and gas industry
EI -	El Model Code of Safe Practice Part 21: Guidelines for the control of hazards arising from static electricity

Other Publications
National Fire Protection Association	NFPA 30 Flammable and combustible liquids code.
UL 2085	Protected Aboveground Tanks for Flammable and Combustible Liquids

UK SI 1998 No.2307	The Lifting Operations and Lifting Equipment Regulations 1998
SI 2001/2954	Control of Pollution (Oil Storage) (England) Regulations 2001
UK SI 2002 No. 2776	The Dangerous Substances and Explosive Atmosphere Regulations 2002
SSI 2011/209	The Water Environment (Controlled Activities) (Scotland) Regulations 2011
WSI 2016/359	The Water Resources (Control of Pollution) (Oil Storage) (Wales) Regulations 2016

11

NISR 2010/412	Control of Pollution (Oil Storage) (Northern Ireland) Regulations 2010
SSI 2017/389	The Water Environment (Miscellaneous) (Scotland) Regulations 2017
UKSI 2016/1154	Environmental Permitting (England and Wales) Regulations, 2016
NISR 2009/254	The Groundwater Regulations (Northern Ireland) 2009
UKSI 2009/2902	The Groundwater (England and Wales) Regulations 2009
CIRIA 535	Above-ground proprietary prefabricated oil storage tank systems.
CIRIA C736:2014	Containment systems for the prevention of pollution. Secondary, tertiary and other measures for industrial and commercial premises
OFTEC document T19	Domestic Oil Tank Bases Construction and Design
EEMUA 186	EEMUA Publication 186 A Practitioner’s Handbook for potentially explosive atmospheres

12

1.5	Abbreviations
AFI	Ancillary Fuel Installation
AP	Authorised Person
ATG	Automatic Tank Gauge
BF(G)	British Forces Germany
BS	British Standard
CAFM	Computer Aided Facility Management
CDM	Construction Design and Management Regulations 2015
CESO	Chief Environment and Safety Officers
CFFP	Certificate of Fitness for Purpose
CO	Commanding Officers
DIO	Defence Infrastructure Organisation
DSEAR	The Dangerous Substances and Explosive Atmosphere Regulations 2002
EA	Environment Agency
EFM	Estate Facilities Managers
EI	Energy Institute
ERA	Environmental Risk Assessment
EWR	The Electricity at Work Regulations
FAME	Fatty Acid Methyl Ester
FDIS	Future Defence Infrastructure Services contract.
FGSR	Fuel Gas Safety Regulator
GRP	Glass Reinforced Plastic
HB	Handover Board
HDPE	High Density Polyethylene
HoE	Head of Establishment
HSE	Health and Safety Executive
IP	Ingress Protection rating as defined by BS EN 60529
LQA	Land Quality Assessment
MMO	Maintenance Management Organisation
MOD	Ministry of Defence
MWC	Maximum Working Capacity
NFPA	National Fire Protection Association
OA	Operating Authority
OWI	Oil Water Interceptor
PVV	Pressure/Vacuum Valve
RCBO	Residual Current Breaker with Over-Current
SB	Siting Board
SEFM	Senior Estate Facilities Managers
SEPA	Scottish Environmental Protection Agency
SFG20	Services and Facilities Group 20
SOR	Statement of Requirement
SPZ	Source Protection Zone
SRP	Safety Rules and Procedures
TA	Technical Authority
TS	Technical Services
TS-Pet-01	Technical Standard – Petroleum - 01
TS-Pet-02	Technical Standard – Petroleum - 02
TS-Pet-03	Technical Standard – Petroleum - 03
TS-Pet-04	Technical Standard – Petroleum - 04
USVF	United States Visiting Forces
VOC	Volatile Organic Compound
13

1.6	Definitions
The terms used within this Guide are defined below:
Above ground tank: Tanks that are not buried or mounded and where all sides are visible for inspection, allowing that access to the tank base may be compromised by its supporting structure. They may be located in a pit below ground level at ground level or raised above ground level.
Above ground pipework: Pipework that is not buried or hidden and where all sides are visible for inspection, allowing that access will be limited by pipe supports.
Authorised Person: The AP is the individual responsible for the practical implementation and application of JSP 375 Volume 3 for the systems, installations and locations for which they have been appointed.
APEA/EI Blue Book: The use of the term ‘Blue Book’ throughout this Standard refers specifically to the Energy Institute and Association for Petroleum & Explosives Administration standard – The Design Construction Modification Maintenance & Decommissioning of Filling Stations.
Bund: A wall of appropriate height constructed of concrete, metal or other suitable material, designed to contain and confine spillage of oil from any cause.
Check Valve: A valve which shall only allow flow in one direction.
Class I, II & III (Fuel): Energy Institute classification of petroleum products graded by the product’s flash point. Class I has a flashpoint below 21 deg C (i.e., petrol), Class II has a flashpoint of 21 to 55 deg C inclusive (i.e., kerosene) and Class III has a flash point of 55 to 100 deg C inclusive (i.e., diesel).
Class I, II, III, IV, V, VI (Leak prevention and Detection): Leak detection of Underground Storage tanks and pipework as per BS EN 13160 Parts 1-7.
Class I & II (Electrical): Class I appliances have protection from basic insulation and earth
connections. Class II appliances have at least two layers of insulation, also known as double insulated.
Competence: The ability to put skills and knowledge into practice in order to perform a job in an effective and efficient manner to an established standard.
Competent Person: A person with sufficient technical knowledge or experience to prevent danger or, where appropriate, injury, during their work.
Contractor: The company employed to carry out installation or maintenance work on an AFI. The Contractor is to have a suitable background in fuel infrastructure and demonstrated history and experience in forecourts and or MOD AFIs.
Deflagration Flame Arrestor: Primary function is to allow the flow of gases or vapour of flammable liquids through the enclosure but prevent the transmission of a flame from the outside. Must be ATEX certified.
14

Designer: The company employed to carry out the planning and design work on an AFI. The Designer is to have a suitable background in fuel infrastructure and demonstrated history and experience AFIs. The Designer must also meet the requirements for a designer as specified within the CDM Regulations.
Explosive Atmosphere: A mixture of air, under atmospheric conditions, and flammable substances in the form of gas, vapour or mist in such proportions that it can be exploded by excessive temperatures, arcs or sparks.
Equipment Certification: Equipment for use in Hazardous Areas is ATEX certified by one of a number of testing authorities (Notified Bodies) as meeting the requisite standards. This certification is arranged by the manufacturer of the equipment.
Flame Arrestor: See Deflagration.
Gross Capacity: Is the total volume of the tank as provided by the tank manufacturer. Gross capacity is synonymous with brim-full capacity or the point at which the tank overflows into the bund.
Hazardous Area: An area where a flammable or explosive gas or vapour-air mixture (often referred to as an explosive gas-air mixture) is, or may be expected to be, present in quantities which require special precautions to be taken against the risk of ignition.
Integrally Bunded: A storage tank that has a twin wall constructed around the primary tank to provide secondary containment in the event of tank failure. Where all the ancillary equipment associated with the tank is installed within the secondary containment. The terms twin-skinned, double walled are synonymous with integrally bunded.
Kerosene-Based Products: Products conforming to BS 2869 Class C1 or C2 with or without the addition of biofuels which have a flash point of 38 deg C or above.
Leak Detection System: Automated systems to detect product leaks from existing tanks and pipes to the surrounding environment.
Leak Prevention System: Secondary containment systems for tank and pipes that prevent any leaking fuel form being released to the environment, with associated positive
monitoring that provides an alarm when a breach of containment is detected.
Maximum Working Capacity: Is less than the gross capacity of the tank. It is the maximum volume of fuel that can be safely contained in a tank allowing for thermal expansion and when road tanker unloading is taking place, time to respond to an emergency situation such as an overfill alarm, and the drainage of the pipework and hose from the shutoff valve into the tank. This capacity should vary dependent on the tank size and whether the tank is below or aboveground. Every tank should be labelled to show its maximum working capacity. Maximum working capacity is synonymous with safe working capacity and nominal capacity.
Non-hazardous Area: An area in which an explosive atmosphere is not expected to be present so that special precautions for the construction and use of the electrical equipment are not required.
Operating Authority: The line manager of the Fuels and Lubricants section has delegated authority for the installations, in accordance with the current version of JSP 317. Authority must be given by the OA before any works can be undertaken on a Petroleum Installation.
15

Overfill Prevention Device: A device or system designed to automatically shut-off and prevent a delivery of fuel overfilling a tank beyond its maximum working capacity.
Pressure/Vacuum Valve: A dual purpose valve which automatically prevents excessive positive or negative pressure in the tank or pipe to which it is connected.
Oil Water Interceptor: A device installed in a surface water drainage system to separate out any fuel and thus prevent it reaching public drains, sewers or water courses. The terms separator and interceptor are synonymous within this Standard.
Professional Inspector: The person responsible for inspection of petroleum facilities as
specified within the Technical Standard Petroleum 03 Professional Inspection of Fuel Infrastructure and Flammable Dangerous Goods Stores.
Services and Facilities Group 20: (SFG20) Schedules produced by Building Engineering Services Association (BESA) including MOD specific standard maintenance specification for buildings.
Siting Board: Meeting convened with all responsible stakeholders, to be convened by the Head of Establishment (HoE) or Representative and run in accordance with JSP 850 & 317.
Tanker Delivery Stand: Paved area where refuelling bowsers park to fill storage tanks. May be a paved area is either bound or laid inside an area of containment with a fall to drainage which is connected to the buried OWI where installed.
Technical Authority: Branch of DIO with responsibility for providing authoritative technical works advice.
Striker Plate: A pad fitted at the location hat the dip stick or tape end strikes the tank bottom to provide reinforcement and avoid damage to the tank shell.
Wet Stock Management: A system for checking and keeping records of the fuel stored, delivered and dispensed and comparing them to identify any discrepancies which might indicate an unexplained loss of product.
2.	Application of This Standard Elsewhere
2.1	USVF Bases
2.1.1 The guidelines given in this Standard are applicable to installations found on MOD Establishments occupied by the United States Visiting Forces (USVF).
2.1.2 Both in terms of quality and safety, the Standard of work undertaken on USVF sites shall not be inferior to those executed on the UK MOD sites.
2.2	Overseas Estates
2.2.1 The Secretary of State has stated that; “Within the United Kingdom (UK) we comply with all applicable HS&EP legislation” and that “Overseas we apply our UK arrangements where reasonably practicable and, in addition, respond to host nation’s relevant HS&EP expectations”.
2.2.2 The estates occupied by BF(G) apply their own local (German) regulations. The competency of the contractor is established prior to contract let and local procedures apply to the selection
16

and appointment of the Competent Person. For this reason, while the general principles mentioned in this Technical Standard may be applicable, the document will be of limited use to BF(G) staff.
17

3.	Planning
3.1	Statement of Requirement
3.1.1 The user needs to identify what it is they require, normally using the DIO process which starts with a Statement of Requirement (SOR). It is essential that this statement provides a clear and concise requirement that includes details of the volume of product (fuel) that it is expected will be required over a period of a year.
3.1.2 Any known requirements should also be included such as the intended location and any limitations placed on that location i.e. due to explosives facilities or impingement into flight line etc.
3.1.3 Identify the details of the work likely to be undertaken as this will allow identification of the correct stakeholders who will need to be in attendance at the Siting Board (SB).
3.2	Initial Planning
3.2.1 Prior to the siting board taking place it will be necessary to work out the basic concept and requirement for the AFI. This information should be made available to the siting board to ensure the installation has the best chance of being correctly sighted. It is advised that DIO TS be consulted at this stage, to ensure that they are aware of the project and can provide any feedback, including lessons learned from any previous/similar projects.
3.2.2 After consultation with the relevant unit stakeholders (end user, fuels section, HoE etc.), the MMO will produce a set of requirements for anticipated work and technical documentation deliverables that shall form the basis of discussion and agreement for the siting board. As a minimum, the following details shall be recorded in the SOR;
- Number of tanks,
- Capacity of tanks,
- Likely footprint of the site,
- Reason for a buried tank if required,
- Tank pipework proposed routing,
- Fuel polishing requirement and outline specification,
- Known environmental issues at the site proposed,
- Electrical supply location and suitability,
- Existing buried services,
- Scope of any decommissioning or demolition works required.
3.2.3 As part of the initial planning process, health and safety, environmental risk assessments and a baseline Land Quality Assessment (LQA) should be completed to establish the facility requirements to form the basis for stakeholder engagement. These assessments should take into account the following;
- The nature, location and depth of any required waste disposal (landfill) and land contamination,
- Any subterranean water courses, aquifers, culverts, pipelines or mine workings; any cuttings or tunnels and any basements or cellars directly beneath or adjacent to the, AFI.
- Surface waters and groundwater,
- Protected environmental areas, for example a Site of Special Scientific Interest (SSSI).
18

The nature of the previous uses of the land being redeveloped should also be identified and assessed, including where necessary an intrusive investigation.
3.2.4 When redeveloping existing sites remediation may be required. The scope and scale of remediation, if required, should be determined through the LQA process.
3.2.5 Reference should be made to;
- BS 10175 Investigation of potentially contaminated sites Code of practice,
- Land Contamination: Risk Management, (EA, 2020),
- NPPF National Planning Policy Framework (DCLG, 2012) in England, or the relevant planning policies for your country.
3.2.6 Initial planning needs to take into account Environmental Risk Assessment. Reference should be made to oil storage and groundwater protection legislation, it should be noted that an environmental permit may be required or the installation may be objected to by the environmental permitting authority.
3.2.7 Consideration should be given to consultations with responsible public authorities and utility providers during planning where those authorities have jurisdiction within the MOD estate. Consult with the DIO Environmental Ordnance Liability (EOLM) Team (DIOTS-LQA@mod.gov.uk) for SME LQA support as part of this initial planning process.
3.2.8 Follow local procedure to determine if Building regulations are applicable to the project and ensure that appropriate instructions are followed. In relation to Building Regulations and the Defence Fire Safety Regulator requirements of JSP850, the Project Team should forward their proposals and a completed Form 1 Notification of Building Work to the DIO Building Control Compliance Authority Group Mailbox DIOTS-BEHS-worksnotification@mod.gov.uk
3.2.9 All above reference documents are to be included with the handover documentation.
3.3	Siting Board
3.3.1 The Siting Board (SB) is a mandatory requirement. All new permanent and semi-permanent AFI and refurbishments are to be the subject of a properly constituted SB prior to the placing of project management or construction contracts.
3.3.2 The siting Board must follow the requirements of JSP 850 Part 2: Standards and Guidance ‘Acquire and Build’, ‘Siting and Handover Boards’.
3.3.3 It is the responsibility of the HoE (or representative) to arrange for the SB to be held. 3.3.4 A record of the siting approval should be included in the handover documents.
3.4	Risk Assessment - General
3.4.1 The assessment of risks and inclusion of mitigating measures within the design process and operation, is a legal obligation under UK regulations, primarily the Health and Safety at Work etc Act 1974. A duty of care is placed upon the MOD to review the hazards associated with the storage of fuels within the MOD estate, and to put in place measures that either reduce or remove the likelihood of hazards causing harm to their employees or the general public.
3.4.2 It is not the intention of this Standard to provide specific guidance on the procedures relating to the undertaking of Risk Assessments. Those with a duty to assess the risks relating to the
19

design, operation, inspection, maintenance of a facility should refer to the JSP 375 Part 1 – Directive and external UK HSE legislation.
3.4.3 It should be noted that the risk assessment shall be revisited if any changes to the operation or design of the facility are made after initial commissioning.
3.4.4 The following sections 3.5 to 3.8 list subjects, whilst not exhaustive, that should be considered when undertaking a risk assessment of any AFI from the viewpoint of design and maintenance. It shall be noted that they are not listed in any order of priority.
3.4.5 Changes to the management, operation, or design of an existing AFI shall not be initiated without a recorded risk assessment. This shall consider the risks to operability, maintainability, product containment, accessibility, plant reliability and life expectancy, environmental, standard operating and emergency procedures that may be introduced by the change or the new procedure. Records of the change should be documented and maintained for the life of the facility. This should form part of the formal Management of Change system operated at site level.
3.4.6 All risk assessments should be included in the handover documents.
3.5	Risk Assessment - Fire
3.5.1 The likelihood of a major fire can be minimised by good plant design and layout, sound engineering, good housekeeping, good operating practices and proper instruction, supervision and training of personnel. Tank design and layout shall include the provision of adequate water supplies, fire protection and firefighting equipment, means of escape for personnel and means of access for fire & rescue in the event of a fire. The level of protection afforded to AFI will vary dependent upon the size, complexity of the installation at each location. It is important to assess the risk involved at each location and provide and install appropriate fire safety measures for each particular risk. Ensure DIFS is applied.
3.5.2 Specific risks to be considered are as follows;
- Provision of lightning protection,
- Proximity of packed petroleum or gas cylinder stores,
- Adequacy of height of vent pipe,
- Need for deflagration flame arrestor.
3.5.3 The number and location of fire-fighting equipment is to be determined by the Unit Fire Officer.
3.6	Risk Assessment - Environmental
3.6.1 Referred to in this document as an Environmental Risk Assessment (ERA).
3.6.2 Fuels containing hydrocarbon substances are hazardous to the environment. It is a legal requirement to prevent pollution by these substances to the wider environment and unless permitted, their discharge is a criminal offence throughout the UK. The storage and handling of such substances and other pollutants can present a significant and ongoing potential for environmental pollution through accidents, vandalism, theft, poor practice, and the deterioration of storage vessels and associated infrastructure such as pipelines.
3.6.3 Groundwater is particularly at risk and once polluted can become expensive and difficult to remediate. Surface waters such as streams and rivers are particularly at risk from spill incidents and the escape of product can impact biodiversity.
20

3.6.4 The oil storage and groundwater regulations and legislation identified in this Standard at section 1.4 Standards and Regulations ‘Other Publications’ should be consulted prior to the production of the environmental risk assessment.
3.6.5 Specific issues to be considered are as follows;
- Secondary, tertiary containment and the need for an Oil Water Interceptor (OWI),
- Presence and location of existing drains and OWI,
- The need for a Road Tanker Delivery Stand and if it requires an OWI.
- Fitting of overfill prevention devices to tanks,
- Site cleanliness, avoidance of accumulation of rubbish in the immediate vicinity,
- Suitability and sufficiency of leak detection and monitoring system and any associated maintenance routine,
- The need for alarms and gauges necessary to avoid spillage or leakage and the need for these items to be electrically powered to provide alarms.
- Provision of spill kits,
- Monitoring & maintenance required to ensure soundness of tank, during its lifetime.
3.7	Risk Assessment - Construction
3.7.1 Construction works are defined within the Construction (Design and Management) Regulations (CDM) and include construction, alteration, conversion, fitting out, renovation, installation, commissioning, maintenance, repair, upkeep and removal of services. For CDM works procedures, roles and responsibilities refer to JSP 375 Part 2 Volume 1 Chapter 33.
3.7.2 The CDM client or Principal Designer is to:
- Ensure that the design and construction take account of the requirements of JSP 375 Part 2 Volume 3 so they can be satisfactorily implemented throughout the life of the facility,
- Ensure that the effects of the works and the completed installation upon the existing site infrastructure are fully understood and considered so as to ensure continuing compatibility.
3.7.3 At the initial design stage of a project the CDM client and or Principal Designer, HoE and other relevant stakeholders of the works are required to initiate the necessary exchange of pre-construction information and to inform design and build deliberations. The MMO is to ensure key stakeholders within their organisation have been notified and that any issues are identified before work commences. The MMO is to liaise with the Client and or Principal Designer as appropriate. The CDM Client and Principal Designer are to coordinate and manage the flow of health and safety information between all stakeholders in the pre-construction phase of a project. Once the construction phase commences the Principal Contractor takes the lead role for coordination.
3.8	Risk Assessment - Dangerous Substances Explosive Atmosphere Regulations
(DSEAR)
3.8.1 Installations in which flammable substances are handled or stored should be designed, constructed, operated and maintained so that any releases of flammable substance, and consequently the extent of hazardous areas, are kept to a minimum, whether in normal or abnormal operation, with due regard to frequency, duration and quantity of a release.
3.8.2 Prior to the production of the risk assessment the ‘The Dangerous Substances and Explosive Atmosphere Regulations 2002’ should be consulted. See L138 DSEAR ACOP for guidance.
21

3.8.3 To ensure compliance with DSEAR, prior to being placed into use for the first time a risk assessment shall be completed by a Competent Person as well as the manager responsible for the process (JSP 375 Volume 1 Chapter 9). If any potentially explosive atmospheres are identified they must be recorded; this should be carried out using the MOD Form 5014.
3.8.4 Site specific (not generic) hazardous area classification drawings, in plan and elevation with all major dimensions shown should be provided as part of the design and construction process, this will inform the location of ATEX certified equipment for the detail design and will need to be reviewed as part of the DSEAR assessment.
3.8.5 Electrical and mechanical equipment used in a hazardous area is to be suitably rated (ATEX certified) to the zone in which it shall operate, and recorded in a register as part of the design process.
3.8.6 Where the installation is only used for high flashpoint Class III fuels then PG 2018/02 should be used as guidance for the DSEAR risk assessment. This Practitioner Guide sets the Ministry of Defence (MOD) Standard for the consistent compliance with the Dangerous Substances and Explosive Atmosphere Regulations (DSEAR) for high flashpoint Class III fuels on the MOD estate.
22

4.	Design Requirements
4.1	General Design Requirements
4.1.1 The tank, pipework and any pumping installation required, will be undertaken in line with BS 5410-2 ‘Code of practice for liquid fuel firing – Part 2: Installations providing space heating, hot water and steam supply services to non-domestic buildings’, it will be followed for all bulk storage tank installations.
4.1.2 In addition BS 5410-3 ‘Code of practice for oil firing Part 3: Installations for furnaces, kilns, ovens, oil-fuelled standby generators and other industrial purposes’ will be followed for these specialist installations.
4.1.3 Any alterations to, and clarifications of the BS 5410 required by MOD will be identified within this standard. In those areas where BS 5410 offers options, this standard will set the MOD required option. This standard may vary BS 5410 where required, if however, the reader believes this causes a contradiction between this standard and the BS 5410 then it should be brought to the attention of DIO TS immediately for clarification.
4.1.4 For further information on the construction of integrally bunded tanks CIRIA C535 may be consulted.
4.1.5 All concept and detail design requirements should be included in the handover documents.
4.2	Initial Design (Concept Design)
4.2.1 First choice for all installations will be above ground tanks separated from the building that they serve. If operational or safety requirements preclude this, then prior to the design commencing DIO TS agreement should be obtained. As an example, tanks located within a building or that are to be buried should have DIO TS agreement prior to the design commencing.
4.2.2 The positioning of fuel storage tanks shall take into consideration potential incidents that might threaten the installation, or that might affect it or the surrounding buildings or the environment as a consequence of loss or spillage of fuel from the tank. For example; vehicle impact, fire and risk of pollution.
4.2.3 The installation will be designed to minimise the risks from the fuel to any person likely to be at or near the facility.
4.2.4 Storage tanks should be located in a manner that will allow safe access and subsequent removal if required.
4.2.5 Physical impact protection shall be incorporated into the design of all above ground tanks.
4.2.6 Above ground tanks shall be Integrally bunded in such a way that the bund is protected from rainwater ingress, single skinned conventionally bunded tanks should only be used where the issue of rainwater ingress into the bund is satisfactorily addressed by some form of adequate weather protection or water removal system.
4.2.7 Where there is an operational military need or requirement for buried tanks then they must be fitted with interstitial monitoring & Class 1 leak detection.
4.2.8 Spatial Coordination must be considered and a basic design plan will be needed with
23

hazardous areas marked, the design must be reviewed against building regulations where required. Ensure the layout is clear and concise and the concept design is reviewed by the Project team & DIO TS. Make sure the design is economical, safe and effective i.e. nothing in hazardous area that does not need to be there etc.
4.2.9 At an early stage in the planning and design process the criteria for numbers of tanks, tank capacity and layout shall be determined. Factors to be considered include;
- Adequate positioning of fuel storage tanks with awareness from the threat of fire or flammable vapour accumulation,
- Anticipated fuel throughput (new builds),
- Historical fuel throughput (refurbishments),
- Expected and available product delivery cycle,
- Types of product to be stored,
- Method of transfer to consuming equipment (e.g. pumped or gravity).
- Safe access for maintenance and subsequent removal,
- Likely Extents of Hazardous Area,
- The need for electrically powered sensors, alarms and monitoring systems.
4.2.10 Existing available drainage arrangements should be identified and an outline proposal produced for ensuring environmental compliance.
4.2.11 Electrical supply arrangements available should be identified. The installation will require a TN-S or TT supply for any electrical equipment installed in a hazardous area.
4.2.12 Analysis of explosion protection and consideration of prevention or control measures must be carried out at an early stage by the designer who should possess the required competences to undertake this task. The explosion protection analysis & hazardous area classification study must include the identification and calculation of DSEAR zones. It must identify equipment category requirements for all equipment within the defined hazardous areas along with any necessary design alterations required to the initial design. Design risk assessments for specific items of equipment intrinsic to the effective operation of the design should be obtained from suppliers to inform the process.
4.2.13 At the design and planning stage the risks and hazards associated with operation and maintenance of the AFI should be identified. Where practicably possible, these risks such as working at height, should be removed through a risk-based design approach. Where there is a necessity to access the top of the fuel storage tank for foreseeable repair, maintenance activities and normal operational requirements, a suitable means of access and working platform may need to be included
4.2.14 The ERA should identify the level of protection the tank requires for the location in which it is sited. In addition, however consideration must be given to the maintenance requirements needed to maintain that level of protection to minimise the likelihood of environmental damage whilst maximising equipment safety and the protection of the person. Requirements for ATEX protected equipment, electrical installations and alarm systems should be carefully considered to ensure that the size and location of the tank justifies the additional maintenance requirements associated with this equipment.
4.2.15 The concept of operation for the installation will be included within the handover documents.
4.3	Detail Design requirements for Tanks
4.3.1 Tanks should be designed, constructed, and installed so as to provide protection to
24

personnel and the environment from incidents caused by fire, explosion and the release of product. When properly installed the complete system should retain its integrity for the entire duration of its design life. All tanks should have the following essential performance requirements;
- Consideration should be given to HSG 176 during the design of the tank.
- Shall be fitted with a mechanical overfill prevention device to prevent spillage of product during tank filling compliant with BS EN 13616-1.
- Means of protection to prevent degradation due to corrosion, chemical action or fuel incompatibility,
- Means to contain any uncontrolled release of fuel or vapour,
- Designed to provide means to test the soundness off any bund or interstitial space,
- Means to identify if any product has leaked into the bund or interstitial space,
- Accessibility for routine and essential maintenance,
- Ease of demolition or relocation,
- Tanks shall have a certificate of conformity supplied by the manufacturer to confirm compliance with the requirements of the appropriate BS standard to which they were designed and constructed. The certificate may include details of class, certifying authority's approval number, client, job number and site. It should also have details of the number of compartments and their capacity, test pressure of tank and of skin exterior finish, interior finish, thickness of any exterior protective coating and interstitial space volume. It should be signed on behalf of the manufacturer,
- All tanks are to be designed (In addition to BS 5410) to enable remote internal cleaning to be undertaken. Where in exceptional circumstances personnel entry to the tank is required a manway of 800mm min inside diameter will be specified and reference is to be made to TS-Pet-01 for guidance on associated access issues. Prior to design commencing agreement of DIO TS is to be obtained,
- In addition to the requirements of BS 5410 tank distance from other tanks or buildings will be as per JSP 317 Pt 2 Vol 1 serial 77 table 2.1.6.1,
- Where it is envisioned that access to the tank for refuelling may be required during the hours of darkness suitable and sufficient lighting should be installed using low energy technology lamps which are located outside any hazardous area and will illuminate the fill point, tank contents gauge and vent,
- All above ground and buried tanks shall (in addition to BS 5410) be installed with a suitable proprietary means to drain water from the tank. Note! to cope with Biofuels this should be by suction and drop line, the bottom drain off cock of an above ground tank is not used for this purpose,
- All tanks will have facilities installed to enable a fuel sample to be taken from within the tank i.e. not from the supply line or drain valve,
- All sensors needed will have any openings required installed during construction ready to accept the sensors, the tank must not be altered on site post-delivery to accept them,
- ‘Striker plates’ will be fitted to align with the dip stick/tape location,
- Isolation valves shall be fitted to allow the tank to be isolated from the pipework system and to allow servicing of pipe work and individual components such as pumps and filters. These valves will be designed to be locked in the ‘Closed’ position using a padlock and where required drain valves should be lockable in the ‘Open’ & ‘Closed’ position.
4.3.2 In addition, above ground tanks should have the following additional essential performance requirements;
25

- Tanks should be Integrally Bunded, and have allowance for the fitting of a secondary containment bund alarm/indicator, visual confirmation of liquid level must be possible,
- Integrally bunded tanks must be constructed so that the soundness of the bund can be tested as and when required,
- Where a separately bunded tank is used for tanks above 10000ltrs a bund alarm will be fitted even where effective weather protection has been provided,
- The bunds of Integrally and separately bunded tanks should be so constructed as to allow suitable and sufficient access to empty and clean the bund,
- Tanks up to 3500ltrs may be of plastics or steel as per BS 5410,
- Tanks above 3500ltrs and up to 10000ltrs will be manufactured of steel unless expressly allowed by the project manager and DIO TS as per BS 5410,
- Tanks above 10000ltrs will be of steel manufacture as per BS 5410,
- Tanks should be installed so as to enable access to the underside of the tank (or bund) for inspection purposes, they should be installed on a skid, saddles or concrete piers providing at least 300mm height from tank underside to foundation level. The tank shell or its bund shell are NOT to be placed in direct contact with the foundations as is allowed in BS 5410. Where the skid is welded to the tank the base of the skid shall be protected where it contacts the foundation in the same manner that is used to protect the tank shell from a brick or concrete pier.
- Will be fitted with anti-syphon device on the delivery pipework (non-return valve), installed on the tank delivery pipe within the bund, were available and where compatible with the fuel using device proprietary anti-syphon devices will also be fitted within the bund to delivery lines.
4.3.3 In addition, buried tanks should have the following additional essential performance requirements;
- Buried tanks shall be of double skinned type with an interstitial space monitoring system which constantly monitors for leaks using a Class I leak detection system to BS EN 13160 including an automatic alarm with suitably visible and audible qualities that will ensure it is not ignored,
- In addition to that specified in BS 5410 buried steel tanks can be constructed to BS EN 12285-3 Workshop fabricated steel tanks - Part 3: Horizontal cylindrical single skin and double skin tanks for the underground storage of flammable and non­flammable water polluting liquids for heating and cooling of buildings,
- In addition to those tanks specified in BS 5410 buried GRP tanks where allowed by DIO TS will be specified in accordance with the APEA/EI ‘Blue Book’ Design Construction Modification Maintenance & Decommissioning of Filling Stations.
4.3.4 In addition to the above where the tank is above 10000ltrs in size or it is required by the ERA, the fuel supplier or the design then it will be fitted with the following:
- A high-level alarm,
- A low-level alarm,
- A bund alarm.
4.3.5 Before leaving the manufacturer's works, tank tests shall be undertaken in accordance with the tank design code and manufacturer's standard procedure;
- Results of pressure tests of both shell and bund/interstitial space should be provided prior to the shipping of the tank.
- Any tank deformation allowed by the manufacturer for installation will not exceed the manufacturers guidance during transport, hoisting and installation and will be
26

confirmed satisfactory once in position and where required backfilled. Particular care must be taken with tanks fabricated from GRP or Plastics.
4.3.3 Tank Labelling and marking all tanks should carry a label containing their details in accordance with serial 6.0 of this standard.
4.4	Tank & pipework Painting and Coating
4.4.1 Painting and Coating
- Where surfaces of steel tanks are to be painted on site weather protection will erected as required to ensure that they shall be clean, dry and free from rust prior to painting,
- After tank erection and satisfactory completion of tank testing, patch painting to the original tank specification will be undertaken,
- On completion of the tank coating (where applied) and other internal work, the interior of the tank shall be left clean, dry and free from foreign objects and in all other respects, fit to receive fuel.
- For normal installations internal tank lining is not a requirement unless specifically requested. If required BS5410 provides some limited guidance and TS-Pet-01 can be referenced.
- Note that zinc rich paints and coatings should not be allowed to come into contact with the product in normal operations.
- Buried carbon steel tanks will be externally coated, guidance for tanks is provided in BS5410. Coal tar based hot applied products and Bitumen coatings will not be used, proprietary epoxy, glass fibre, polyurethane, or PVC coatings suitable for the ground conditions encountered are acceptable.
- Note ‘Holiday testing’ cannot be carried out on coatings which are zinc rich.
- Tanks will not normally be concrete encased. Where buried tanks are to be concrete encased the tank coating will be reviewed prior to application to ensure that the corrosion resistance of the coating will not be reduced.
- All above ground cardon steel tanks will have a suitable anticorrosive external primer coating applied at the factory. The primer coating will comply with BS EN ISO 12944-5:2019 and will be at least Zinc-Rich (80% by mass in dry film) as defined by that Standard. After installation at site an inspection will be carried out and any touch up or repair will be made in coating products that match the original applied at the factory or that have been approved by the original coating manufacturer as suitable for site touch up. This must maintain the original protective standards of the product.
- The tank surface must be prepared as required by the coating manufacturer prior to the application of the primer coat at the factory and for damage repair and touch up at site.
- All above ground carbon steel tanks will in addition to having a primer coating applied, have a top/finish coating applied which is suitable for use with the primer coating, is highly resistant to the product being stored and able to protect the primer coating from the stored product. This will be applied to the tank either at the factory or at site. Where factory applied a site inspection will be carried out after installation and any touch up or repair will be made in paint products that match the original applied at the factory or that have been approved by the original coating manufacturer as suitable for site touch up. This must maintain the original protective standards of the product.
- Above ground carbon steel pipework should have a protective coating applied matching that of the above ground carbon steel tank allowing that application at site may be unavoidable.
- Where the location of the installation means that extreme climatic conditions will be encountered (such as salt water) then the additional protection required should be
27

risk assessed and adjustments made to the coating specification. Reference can be made to TS-Pet-01 for further guidance on coatings.
4.5	Detail Design requirements for Tank Vent Pipes
4.5.1 Vent pipes shall be located so that vapour should be dispersed safely into the atmosphere. Locations shall take into account conditions at or near the installation which could adversely affect safe dispersal of any discharge (e.g. the height and location of surrounding buildings). The vents for both kerosene-based products and Class III products tanks must discharge within the bund.
4.5.2 In addition to the requirements of BS 5410 where fuel is delivered via gravity then vent pipes shall extend to a height greater than the maximum liquid level in any road tanker likely to deliver fuel. The vent discharge point shall be a minimum of 3 m from building apertures or the installation boundary.
4.5.3 Vent pipes will be sized as per BS 5410 and BS 799-5 to avoid a build-up of pressure within the tank beyond its design pressure during foreseeable operating conditions such as tank filling and will be at least as large as the incoming fill pipe to act as an overflow in case of tank overfilling. Further detail on vent design may be obtained from BS EN ISO 28300.
4.5.4 All vents will be complete with weather proofing cowl and wire mesh screen of corrosion resistant material to prevent ingress of birds, leaves etc. Mesh to have a maximum hole size of 6mm.
4.5.5 Consideration should be given to the fitting of desiccant dryer air vents especially where ambient humidity is high.
4.5.6 Deflagration flame arrestors will be fitted to kerosene-based products tank vents unless specifically excluded by the fire risk assessment. Flow/capacity will be as per design calculation or 300% of free vent flow/capacity whichever is greater. They will comply with the requirements of BS EN ISO 16852.
4.5.7 Pressure/Vacuum valves (PVV) are not required on tanks unless the ambient temperature is expected to be above the product flash point. Where these are required, reference will be made to TS Pet 01 for guidance.
4.6	Detail Design requirements for tank foundation and bund
4.6.1 Civil ground works including tank foundation will be carried in compliance with the tank manufacturers guidance and the requirements of BS5410, the design of the tank base will be undertaken to support the weight of the tank when full and according to the following guidance
- For tanks of 3500ltrs or less they should be designed according to OFTEC document T19 ‘Domestic Oil Tank Bases Construction and Design.
- For tanks above 3500ltrs they shall be designed in accordance with BS EN 1992-1­1. As a minimum it shall have a reinforced concrete raft of minimum thickness of 100mm which projects beyond the tank (including any integral bund) by a min of 300mm.
- Buried tanks will not normally be concrete encased, they will however have a reinforced concrete raft designed in accordance with BS EN 1992-1-1:2004+A1 :2014 Eurocode 2: , BS 8500:2019and will be installed as per the requirements of BS EN 12285-1 Annex A.
28

Guidance on bund arrangements can be found in CIRIA document C736:2014
4.7	Detail Design requirements Road Tanker Delivery Stand
4.7.1 A safe position from which the road tanker can deliver fuel to the storage tanks shall be identified on the ground with marking paint or other proprietary means.
4.7.2 The tanker stand and the adjacent tank fill point(s) shall be positioned to allow the tanker to discharge without being at risk from other vehicle movements.
4.7.3 Access and egress of the tanker should be achieved without having to make a reverse manoeuvre.
4.7.4 Where it is envisioned that the AFI may need to be refuelled during the hours of darkness suitable and sufficient lighting should be installed using low energy technology lamps which are located outside of any hazardous area.
4.7.5 Where construction of a hardstanding for the road tanker delivery stand is required by the ERA (serial 3.6.5) then it should be designed in accordance with BS EN 1992-1­1:2004+A1:2014 Eurocode 2, BS 8500:2019, BS EN 124 Part 1 and BS EN 1610.
4.8	Detail Design Requirements Fill Points
4.8.1 Labels shall be fixed adjacent to all tank fill points stating the tank identifier (number), fuel type and the maximum working capacity of the tank. This label shall be securely fitted around the fill pipe located at the tank, within the respective access chambers or at an off-set fill point.
4.8.2 The fill points for storage tanks should be positioned adjacent to the road tanker delivery stand. All fill points will be located within secure cabinets and suitable drip tray fitted, excepting those incorporated into the lid of a buried tank (described as direct fill). They may be positioned remote from the tank (often described as offset) with a connecting fill pipe or fitted to the side of an aboveground tank within a fill point cabinet.
4.8.3 To mitigate against overfilling of the tank the tanker driver located at the tanker pump control position to control the filling process must have line of sight to the tank contents gauge and the tank vent if no overfill prevention device and alarm is fitted.
4.8.4 Where an Overfill prevention device is fitted identification sign should be present at the fill point. The sign should include instructions for depressurising delivery hose prior to removal.
4.8.5 For installations containing kerosene a static earth bonding connection or reel may be required, (see also 8.8.3) this requirement should be considered and clarified with the fuel supply company prior to detail design starting.
4.9	Detail Design Requirements for Pipework
4.9.1 Where possible all pipework systems should be of the above ground type, however it is acknowledged that buried pipework has advantages such as providing better fire protection and greater security so may be more suitable for some locations. Where DIO TS approval has been obtained for the use of buried pipework this standard allows for only one type of system due to the environmental implications of pipework damage or corrosion.
4.9.2 Isolation valves shall be fitted to allow the system to be maintained without the need for draining of excessive amounts of fuel from the system during maintenance or servicing of
29

pipework and individual components such as pumps and filters. The location of valves and fittings will meet BS5410 and the extant oils storage regulations. They will be lockable in the ‘Closed’ position and for drain valves in the ‘Open’ & ‘Closed’ position using a padlock.
4.9.3 All buried pipework that distributes fuel to or from a storage tank, whether by suction, gravity or pressurised feed, shall be of the HDPE ‘pipe in pipe’ double containment type in accordance with BS EN 14125 and:
- Conductive pipes will be used and integrated into the design unless excluded by the designer on electrical safety grounds.
- The interstitial space will be monitored by a Class I leak detection system connected to a functioning alarm system as per BS EN 13160.
- Transitions between the HDPE double containment pipe and above ground steel pipes shall be achieved through the use of a proprietary steel transition fitting. The fitting shall be for a screwed type connection. The transition should be located aboveground and as close to the ground level as possible but allow for installation and maintenance,
- All HDPE connections shall be made in accordance with the pipe manufacturer’ instructions,
- Where possible pipework should be buried at a depth of 500mm and located 500mm from all other services,
- Warning tape should be buried above the pipe 150mm below the finished ground level.
- Detailed requirements of burial method, process and backfill will be as specified by the pipework manufacturer.
4.9.4 All above ground pipework has the advantage that leaks are more readily detected, inspection, maintenance and repair is easier and corrosion can be more readily identified and controlled, however containment must still be addressed. Pipework will be constructed in line with BS 5410 part 2. Aboveground pipework and its supports may be at risk from damage particularly from vehicles. The layout of the installation shall minimise the risk of physical damage from vehicles through the use of impact protection such as barriers or bollards.
4.9.5 All above ground pipework must be suitably robust or protected so as to avoid foreseeable damage being caused during maintenance or operation.
4.9.6 The AFI design shall allow for differential movement between tanks and pipework to allow for temperature changes in tanks or settlement. Piping supports should be designed to suit the piping.
4.9.7 Above ground pipework should be pressure tested in accordance with BS5410. A suitable and sufficient risk assessment must always be completed prior to the undertaking of these tests and where required HSE GS4 can be consulted for guidance. Final testing using liquid product should be at 1.5 times the design working pressure or 2 bar whichever is the greater, the test should be left in place for 30mins and there should be no visible change in pressure (+/- 1 psig). These tests should be witnessed by the project managers representative and a certificate produced documenting the proof test & this should be included in the handover documents. Note that allowance for the effects of temperature on pressure must be made during these tests.
4.9.8 All pipework should be labelled with the product it contains and the direction of flow of that fluid at regular intervals of at least 3m along the length of the pipework. Labelling of pipework see serial 6.0 of this standard.
30

4.9.9 Exposed steel pipework outside the bund should where possible employ welded connections to limit potential leakage of product, however where not explicitly excluded by the ERA and allowed by the oil storage regulations screwed joints are permissible. The use of flange connections should be limited to joints with other apparatus that are supplied with flange connections only and shall only be permitted over impervious areas which are part of the tank bund or in an OWI intercepted drainage area.
4.10 Detail Design requirements for Pump systems
4.10.1 In addition to the requirements of BS 5410 for pumping systems designed to supply product to the consuming system. These systems will for a Class III product comply with PG 2018­02, the system will not exceed a pressure of 1 bar gauge at any point within the system. Class II systems should only be considered in exceptional circumstances and where DIO TS have given prior agreement for their usage. If Class II systems are allowed the application of full ATEX and DSEAR requirements will be required and TS-Pet-01 should be consulted for guidance. The number and size of hazardous areas for Class II pumped systems can be expected to be considerable.
4.10.2 Where due to operational constraints it is necessary to exceed 1 bar pressure within the pumped system then DIO TS approval must be obtained before the detail design is completed and consideration must be given to the hazardous area that will be created by the flammable mist that could be created and appropriate hazardous areas should be determined and applied to the design.
4.10.3 Particular consideration must be given to ensuring that the product is not heated to within 10 deg C of its flash point by any of the equipment installed in the system.
4.10.4 Avoidance of pumping to an overflowing tank. Where due to operational constraints it is not possible to comply with BS 5410 requirements for pumped systems with regard to management of vent pipes then to ensure a spill cannot occur during automated filling of a day tank from a storage tank additional fail-safe Interlocks must be fitted. ATEX protected when within a Hazardous zoned area. Electrical circuits must be interlocked as fail safe to ensure that any loss of signal or lack of flow results in shut down of the fuel transfer system. To avoid leakage due to pipe failure it will also ensure that excess flow results in shut down. Allowance must also be made for the contents of SA 2021/02 when designing these systems.
4.10.5 Any pumped system installed will be shut down on receipt of a low-low level alarm condition from the tank from which it is drawing.
4.10.6 Duty and standby pumps will be fitted.
4.10.7 In addition to requirements of BS 5410 air vents and relief valves fitted to pumped system pipework should be risk assessed to identify if they will produce a flammable vapour or mist during operation and design measures implemented to mitigate this hazard by safe venting or a piped return to tank.
4.11 Detail Design requirements for Polishing Systems
4.11.1 If due to concern about fuel turnover/volume or ambient conditions effecting fuel quality fuel polishing systems are specified for Class III systems in addition to inline filters, then in addition to the requirements of BS5410 the following should be considered.
31

- Like all pumped systems pressure should be limited to 1 barg where possible. Where this is not possible and if the system is supplied as a package the manufacturer of the package should provide hazardous area zoning information,
- Identify the need for ATEX protection when within a Hazardous zoned area,
- In addition to any other operational requirements the system must be able to remove suspended water from the fuel, it must be a filter water separator (FWS).
- Easy to remove, replaceable filter elements should be fitted.
- FWS type systems will require a manual or automatic water drain that must be arranged so as to ensure environmental compliance.
- A system to identify high differential pressure and produce an audible and visual alarm should be fitted on recirculating systems, consideration should be given to how this system will be monitored for effective operation. A remote alarm may be required see below.
- Automatic control and associated fail safes will be needed in addition to that for pumped systems. Consideration must be given to the fact that the system will be operating completely autonomously and so alarms may have to be relayed to a separate location to ensure effective operation,
- The standard to which the fuel should be polished should be determined by risk assessment. Consider the flow of fuel through the unit compared to the volume of stored fuel, the quality of fuel required for the fuel using appliance and the level of assurance of fuel quality required.
- Where it is determined that fuel polishing is required then as a minimum fuel quality should meet the requirements of 13.2 Fuel Quality.
4.12 Detail Design requirements for classification and control of a hazardous area
4.12.1 Hazardous zones should be determined in line with L138 ACOP DSEAR and associated industry guidance by a suitably competent engineer, experienced in this area.
4.12.2 Site specific (not generic) hazardous area classification drawings, in plan and elevation with all major dimensions shown should be provided, this will inform the location of ATEX certified equipment for the design and will need to be reviewed as part of the DSEAR assessment.
4.12.3 Following a DSEAR Regulation 5 Risk Assessment, if Equipment Protection Levels (EPL)/ATEX categories vary from that normally expected they are to be marked on the area classification drawing (produced as per DSEAR regulation 7) and recorded within the associated source of release table (BS EN IEC 60079-10-1, Hazardous area classification data sheet – Part II: List of sources of release).
4.12.4 Where a hazardous area exists around an AFI a method of physical control must be implemented in the form of fencing or other physical barriers that will separate personnel, vehicles and exclude any possibility of a source of ignition from coming into contact with the hazardous area.
4.12.5 Note! All works must be controlled in accordance with this standard ‘1.3 Safety’. 4.13 Detail Design requirements for Drainage System
4.13.1 The initial planning of the installation should assess the usage of the facility to establish possible contamination of the drainage system and the likelihood of contaminates entering public drains and sewers, water courses and surrounding land. The risk assessment should consider the products (e.g. petrol, diesel, washing detergents, and other effluents) that may
32

be used, and which may enter nearby drainage systems. In addition to the requirements of BS 5410 the ERA should identify if there is a need for an OWI.
4.13.2 If an OWI is assessed as being required, then it is expected that the provision will be undertaken in line with the requirements of the Aquatrine provider and as such this standard does not provide any further detail information on this subject other than to comment on those parts of the system that will impact the AFI such as vent pipes.
4.13.3 Where the OWI is the responsibility of the project and will not be specified by the Aquatrine provider then the OWI will meet the requirements of BS EN 858 and for further guidance consult JSP 317, Part 2, Vol 1, Chapter 7 ‘Guidance on Operation of Oil Water Interceptors/Separators (OWI) (OWS) on MOD Estate’ & TS-Pet-04.
4.13.4 Where the drainage system is the responsibility of the project then gully tops and manholes will meet the requirements of BS EN 124 Part 1 & design of drains will meet BS EN 1610 Construction and testing of drains and sewers.
4.13.5 OWI vent pipes shall extend to a minimum of 2.4 m above ground level and be located a minimum of 3 m from access roads or building openings.
4.14 Detail Design requirements for mechanical & electrical ducts
4.14.1 In addition to the requirements of BS 5410 duct systems for buried pipework & electrical cables should be designed to prevent the transfer of flammable liquid, vapour or gases between potential spillage areas and buildings or other confined spaces on site. All ducts should be sealed at both the point of entry and point of exit with a designed mechanical seal or suitable compound or other filler material which has been proved to provide effective sealing and is resistant to Volatile Organic Compounds (VOCs) in liquid or vapour form. Seal/sealant/compound must be resistant to all compounds present in the product to be stored.
4.15 Detail Design requirements for Fire Fighting Equipment
4.15.1 In addition to the requirements of BS5410 a Fire Risk assessment is to be carried out as per serial 3.5 of this standard, DIFS & NFPA 30 may be of assistance. Where a life safety risk is identified additional specific guidance should be sought from a suitably qualified Fire advisor. Agreement on the required quantity and provision of portable firefighting equipment will be via the unit fire advisor.
4.16 Detail Design requirements for Warning and H&S Notices
4.16.1 In addition to the requirements of BS 5410 MoD specific signage will be applied at all AFI. Refer to section 6 of this Standard for further details of warning signage. Noting the need for hazardous area signs to define a hazardous area where one exists.
4.17 Detail Design Requirements for Level Measurement & Contents Gauges
4.17.1 To clarify the requirements of BS 5410 All tanks or compartments shall be provided with both a Dipstick (or Dip Tape) and a tank content’s display system for ascertaining the quantity of fuel stored. This tank contents display should be visible both at the tank location and to the tanker driver during loading.
4.17.2 The mechanism for transmission of a signal from a sensor to a local display or alarm will be of a secure and reliable nature, preferable of a direct connection type providing a high level
33

of reliability and it will not rely on battery power alone. Battery backup supplies to a primary electrical supply are acceptable.
4.17.3 For tanks above 3500ltrs in addition to the requirements of BS5410 dipsticks or dip tapes should be calibrated to a specific tank or compartment and
- should be marked with that tank or compartment number and should show the tank maximum working capacity,
- They shall be marked with calibration markings in millimetres and litres at increments of at least 5mm & 100ltrs and be provided with associated tank volume calibration charts (Strapping tables),
- Dipsticks and tapes should be suitable for the tank and the fuel contained e.g. made from a none sparking material for hazardous areas and will not generate static or are earthed prior to use,
- Where it is necessary to provide a safe location to use the dipstick at the tank top, refer to section 5 for guidance relating to the design of access stairways and working platforms,
4.17.4 Tank gauge systems provide an indication of the quantity of liquid contained in a storage tank without the need to access the tank and take manual dip readings. Like dipsticks, the gauge measures the height of fuel in the tank, from which the volume of fuel is then determined. The effects of variations in the properties of the fuel and other factors, which shall influence the measurement of height and computation of volume, can be considered depending on the sophistication of the system used.
4.17.5 The type of tank contents gauge should be determined based on the outcome of the ERA and when all required alarm functions are known as combined units including high and low level alarms etc may prove to be more cost effective than separate units. Varying from solely mechanical to fully electronic they will:
- For tanks up to 3500ltrs a push button sight gauge for bunded tanks and a simple mechanical/float gauge for integrally bunded tanks. Accuracy for reading of mechanical gauge +/- 30mm height of liquid product. Where possible for integrally bunded tanks a second mechanical float gauge of similar accuracy set so that it indicates prior to 1/4 of the bund being full,
- Tanks above 3500ltrs and up to 10000ltrs will have gauges of mechanical/float/clock, pneumatic pump, hydrostatic or electric/electronic type which can achieve an accuracy of indication of +/- 10mm liquid height or 3% full scale deflection of gauge. Where a bund alarm is not fitted a bund indicator of mechanical/float/clock type will be fitted with an accuracy for reading of +/- 30mm height of liquid product set so that it indicates prior to 1/4 of the bund is full or 100mm hight of liquid in the bund has been reached whichever is the more onerous. Serious consideration should be given to the fitting of alarms for the bund and high level,
- Tanks above 10000ltrs will have a mechanical/float/clock, pneumatic pump, hydrostatic or electric/electronic type gauge which can achieve an accuracy of at least +/-2% of volume of product corrected for specific gravity, Low, high and bund alarms will be fitted.
- Pneumatic pump type hydrostatic contents gauges shall be fitted with zero position and range adjustment.
4.17.6 Any electrical or electronic equipment included in such systems and used in hazardous areas should always be certified as appropriate for use the hazardous zone in which it is installed.
4.17.7 Where required by the ambient conditions or fuel supply concerns the tank gauge system shall have the capability of detecting a pre-determined volume of water within the fuel tank.
34

4.17.8 Where it is decided to specify wet stock management with an ATG, consideration should be given to incorporating the above contents displays and alarms into the system to avoid duplication of function, however to avoid a build-up of back pressure the wet stock management system, tank equipment, shall not be installed in the fill pipework
4.17.9 Tank gauge system sensors should never be installed in a fill pipe.
4.18 Detail Design Requirements for Alarms and Controls
4.18.1 In addition to the requirements of BS 5410 where AFI is fitted with an electrical system and/or a wet stock management system a lightweight plastic or GRP enclosure shall be located in an easily accessible position for the environmental protection of these items.
4.18.2 The mechanism for transmission of a signal from a sensor to a local alarm will be of a secure and reliable nature, preferable of a direct connection type providing a high level of reliability and it will not rely on battery power alone. Battery backup supplies to a primary electrical supply are acceptable.
4.18.3 Where tank alarm systems are required by this standard, they must be fail-safe in operation and provide both an audible and visual indication of the alarm. Where AFI are located remotely or in low occupancy areas serious consideration should be given to remote indication of these alarms to a regularly staffed location. The alarms considered for this action should include;
- Tank high level set to operate at least 2% below/before the overfill prevention device,
- Tank low level set to operate at least 100mm above the tank outlet,
- Bund alarm set to operate at the minimum possible detection range of the sensor used but at a maximum of 10% of the bund volume,
- Leak detection alarm set to operate as defined by the manufacturer.
4.18.4 The mechanical overfill prevention device should be set to operate at not more than 95% of tank volume where the maximum working capacity of the tank is 97% of its volume. Dependent upon tank size and the device design it may operate before 95% volume is reached.
4.18.5 In addition to BS 5410 any controls installed as part of the fire valve or fuel pumping system shall be designed to fail safe i.e. to cut off fuel to the fuel using device and to stop pumping from the storage tank on operation or failure. These systems will also provide indication that they have failed. Where the fuel supply to a fuel using appliance will be shut down by the activation of an emergency stop or fire detection system that fuel using appliance must also be shut down by an integrated fail-safe control system.
Working Platforms, Stairways and Access Ladder
5.1	If access is required to any part of the AFI for maintenance or regular adjustment, then suitable access arrangements must be provided. For example, dipping an above ground tank. These structural elements shall be designed and constructed taking account of safe movement around the tank, tasks being undertaken that may require tools to be carried, and other spatial requirements. Loading and local environmental conditions shall be evaluated during the design stage with the structures being designed to BS EN ISO 14122 and other relevant standards referenced within this standard
Labelling and Marking
35

6.1	Tank and Pipework
6.1.1 All tanks and pipework must be labelled with the fuel type and grade they contain using an indelible painting, marking or labelling process and materials that can be expected remain legible and intact for the life of the tank. Where no standard format sign or label exists, a suitable label should be produced including the basic colours and text present on the standard signs & labels identified in this standard.
6.1.2 In addition to the requirements of BS 5410 each tank shall be clearly marked using a durable label which shall be corrosion resistant and resistant to the stored product. The label shall be fixed to the tank on or close to the manhole or fill point. The label shall contain the following information as a minimum;
Tanks designed to BS EN 12285;
- Name and address of manufacturer,
- Year of manufacturer,
- Serial number of tank,
- Tank design standard,
- Maximum working capacity (Nominal capacity),
- Diameter (buried tanks only),
- Tank type,
- Tank material,
- Weight of empty tank.
Tanks designed to BS 799-5;
- Manufacturer’s name or trademark,
- Manufacturer’s reference number,
- Number and date of standard,
- Maximum working capacity (nominal capacity),
- Type of tank,
- Design pressure,
- Test pressure and date of testing.
6.1.3 Aboveground tank signage shall be visible from all angles of approach and include as a minimum;
- Where hazardous areas exist, the entry points to areas classified into zones must be marked with a specified 'EX' sign. (example figure 1)
- Kerosene based products & Class III tanks shall be marked with ‘Flammable’, ‘No Smoking’, ‘No Naked Lights’ (example figure 2)
- Where applicable NATO product and grade identification markings (as per Defence Standard 05-52 Part 2) (example figures 3-6) and the BS Grade of the fuel,
- Tank capacity shall be clearly marked.
36

Fig 1 – Hazardous Areas Sign.	Figure 2 – Tanks Flammable Sign.

Figure 3 – DIESO UK Product Identification	Figure 4 – Marine Diesel F-76 Product
Marking.	Identification Marking.

Figure 5 – KERO A Product Identification	Figure 6 – KERO B(F-58) Product
Marking.	Identification Marking.
6.1.4 Pipework will also be labelled as per NATO product and grade identification markings (as per Defence Standard 05-52 Part 2) (example figures 7 to 10).

Figure 7	Figure 8	Figure 9	Figure 10
6.1.5 Each tank fill point (direct and remote fill points) shall include (figure 11):
- Tank number,
- Maximum working capacity,
- NATO standard product and grade identification marking
- Fuel grade.
37

Figure 11 – Typical Tank Sign at Fill Point(s).
6.1.6 Each tank fill point shall also be clearly marked with the following:
‘DISCONNECT TANKER HOSE’
7.	Requirements for Leak Detection and Containment
7.1	General
7.1.1 A complete leak detection system in accordance with BS EN 13160 shall be incorporated into all buried tank installations. Bunded and integrally bunded above ground tanks should be fitted with suitable and sufficient leak detection but do not have to comply with BS EN 13160. All buried pipework will have a leak detection system incorporated with a BS EN 13160 system.
7.2	System Class
7.2.1 In accordance with BS EN 13160, five class categories are assigned to the leak containment and detection systems, being Class I to V. It is not the intention of this Standard to provide
specific details of each type of Class system, this can be found within BS EN 13160.
7.2.2 The only Class’s specified in this standard is Class I for buried tanks and pipework. This system subjects the storage tank or pipework secondary containment system to a permanent pressure or vacuum test for the life of the installation and will contain leaked fuel within the containment system. The secondary containment shall not allow a release of fuel to ground. Class I are considered inherently safe.
7.3	Leak Containment
7.3.1 All leak containment systems using bund, integral bunding and interstitial spaces will have a test mechanism identified within the design to ensure that that they can have the soundness of the containment proven and that they can be checked for the presence of leaked product. This should include a maintenance process that has been environmentally risk assessed to show compliance with extent legislation. For underground installations this will require continues monitoring of the soundness of the containment as identified above. Monitoring and alarms for above ground tanks will be as identified in other sections of this Standard and the ERA.
38

7.4	Leak Detection
7.4.1 BS EN 13160 Class I leak detection will be fitted to all buried tanks and pipework this will include a pressure/vacuum generator unless otherwise allowed by DIO TS.
8.	Requirements for Electrical Equipment
8.1	General
8.1.1 To ensure safety, it is essential electrical installations are correctly planned, designed, installed, inspected, tested and commissioned.
8.1.2 The electrical installation for the AFI will be in accordance with BS 7671 and the guidance provided in PG 03/09 & PG201 7/02. Where the electrical installation contains a hazardous area DSEAR will be applied and ATEX protected equipment will be required subject to classification of the hazardous area, further guidance is provided within the APEA/EI Blue Book, EI MCoSP Part 1 and EEMUA 186.
8.1.3 The AFI shall be supplied by buried cables (power, telecommunications etc.) suitably protected against mechanical damage and routed outside and not below any hazardous areas. Where risk assessment indicates that the operation of the AFI with hazardous areas may be adversely affected by surges in the supply, surge arrestors should be provided as part of the installation.
8.1.4 A risk assessment should be carried out by the Designer to determine the need for lightning protection of the structures at an AFI. Guidance can be found in EI MCoSP Part 1, EI ‘Guidelines on earthing/grounding/bonding in the oil & gas industry’ and BS EN 62305-3 Annex D.
8.1.5 For all new or refurbished AFI a system earthing installation derived from a shared supply over which the site has no control, shall not be used if the electrical installation is within a hazardous area, if it does then the system earthing shall be derived from a dedicated TN-S system where the supply is direct from the HV Sub Station LV feeder pillar of TN-S type. Where this is not possible an isolating transformer can be used to create a local TN-S system or a TT system with suitable RCD protections can be used. Further guidance is provided within the APEA/EI Blue Book and EI MCoSP Part 1.
8.2	Hazardous Area Classification
8.2.1 Section 3.8 of this Standard provides guidance on the requirements when undertaking a DSEAR risk assessment at an AFI. It is imperative that any Competent Person who provides, maintains or verifies electrical installations and equipment in, or associated with, hazardous areas have a thorough understanding of hazardous area classification. Refer to JSP 375 Volume 1 Chapter 9 for further details of competencies.
8.3	Selection and Installation of Electrical Equipment
8.3.1 Where installed within hazardous zones the electrical installation shall comply with the requirements of BS EN 60079-14, BS EN 60079-25 and BS EN 60079-26 as appropriate. Equipment shall be ATEX certified to a standard suitable for the zone in which it is to be used.
8.3.2 Where electrical equipment is present within a hazardous area within the AFI a test socket should be provided within the electrical control cabinet for the installation, at the origin of the installation supply as specified in the APEA/EI Blue Book.
39

8.3.3 The all-insulated test socket shall be wired to the supply side of the main isolating switch and include a clear and obvious label all as per the 4th Edition APEA/EI Blue Book (see Figure 36 of the Blue Book for diagram).
8.3.4 Within the hazardous area of the installation all fixed equipment should be hard wired to the distribution system. No plugs or socket outlets shall be used to provide power to electrical apparatus.
8.3.5 All electrical equipment will be weather protected by suitable individual IP rating or IP enclosure as per BS EN 60529.
8.4	Location of Electrical Equipment
8.4.1 Vent pipes for tanks or OWIs shall not be used for mounting or securing luminaires, cables, or other electrical apparatus.
8.4.2 Shelters or canopies should be constructed above, and clear of, hazardous areas related to associated apparatus. The selection of canopy luminaires should be in compliance with the Hazardous area assessment and DSEAR risk assessment. However, care should be taken when siting such luminaires to anticipate hazards (such as breakages) which may be created if tanker dip sticks are used beneath the canopy. Also, vapour releases from nearby vent pipes or tanker compartment manholes should be considered.
8.4.3 Where required due to out of hours use the road tanker unloading area, tank gauge and where required dip point shall be adequately illuminated with a minimum design illuminance of 100 lux at ground level. At tanker delivery stands this level of illumination should be achieved with the tanker in the unloading position.
8.5	Electrical Isolation and Switching
8.5.1 Means of isolation and switching shall comply with Regulation 12 of EWR.
8.5.2 Suitable means shall be available for cutting off the supply of electrical energy to electrical equipment, and for the secure isolation of any electrical equipment from every source of supply of electrical energy. Where standby supplies are installed, they require the same isolation and switching requirements as a main supply.
8.5.3 Devices for isolation and control of equipment that are located in a hazardous area shall interrupt all live poles, including the neutral, simultaneously. Devices for isolation and control shall be located in a non-hazardous area.
8.5.4 Devices used for switching off equipment for maintenance purposes are required to have locking-off facilities.
8.6	Main Switchgear
8.6.1 The electrical intake and main switchgear position for the installation shall be located in an easily accessible low fire risk position outside any hazardous areas and kept unobstructed. It shall be fitted with a label identifying the installation it supplies. The main switchgear, test socket and main earthing terminal for the AFI shall be located within a weatherproof GRP cabinet or similar, if not located inside another building
8.6.2 The main switchgear shall incorporate the main isolating switch and the means of secure isolation required by Regulation 12 of EWR. All live conductors of the installation, including
40

the neutral, are to be interrupted simultaneously.
8.6.3 Every circuit for equipment located in a hazardous area which is not intrinsically safe shall be provided with an isolating switch or isolating RCBO in the non-hazardous area for isolation of the equipment from the source of electrical energy.
8.6.4 Where after risk assessment the presence of a hazardous area or the size or location of the installation warrants the addition of an emergency stop facility to supplement the installation isolation switch then an emergency switching device shall be provided to cut off all electrical supplies, including data circuits to all equipment. Means of operating the emergency switching device shall be provided outside of any hazardous areas, visible from all parts of the installation and in particular the loading position and must be readily accessible for rapid operation in emergency (i.e. it should not be positioned more than 2 m above the ground). On larger sites multiple emergency switches may be required to ensure rapid isolation.
8.6.5 The emergency switching device is to be coloured red against a yellow background. Resetting this device alone should not restore the supply. The separate single means of restoring the supply should require manual operation and be co-located with the system main switch gear where it is accessible only by tool or key to authorised persons.
8.6.6 A conspicuous, durable and legible notice shall be fitted adjacent to every emergency switch device that identifies its purpose.
8.6.7 Supplies to essential monitoring equipment, such as leak detection and tank gauging systems, should be installed via individual, dedicated, final circuits. RCBOs feeding such circuits should be clearly labelled and marked 'DO NOT SWITCH OFF'. Isolation for maintenance should require manual operation and be co-located with the system main switch gear where it is accessible only by tool or key to authorised persons, local means of isolation or switching (not requiring a tool or key to operate) should not be provided for this equipment.
8.7	Electrical Overcurrent Protection
8.7.1 Each circuit should be individually protected against fault current and overload by a suitably rated RCBO arranged to break all live conductors including the neutral. This does not apply to data and signalling circuits which are not liable to overload or produce fault currents.
8.8	Protection Against Static Electricity
8.8.1 Providing the continuity of any metal pipework has electrical resistance of 0.01 Ω per m or less and fuel velocity does not exceed 2m/s then fuel flow rates are unlikely to cause a build­up of electrostatic charge capable of presenting a static hazard.
8.8.2 The guidance contained within the APEA/EI Blue Book for ‘Protection against static electricity’ should be followed to ensure that the design of the AFI will mitigate the dangers of static electricity build up on any hazardous areas present. Particular attention should be paid to any separation requirements or static electricity earthing arrangements for above ground and buried parts of the AFI.
8.8.3 Where hazardous areas exist consideration should be given to the need for a bonding connection or reel to be installed at the installation and the fuel supplier contacted for clarification of their requirements.
8.8.4 For further guidance on controlling static electricity at petroleum installations see El Model Code of Safe Practice Part 21: Guidelines for the control of hazards arising from static electricity.
41

8.9	Protection Against Electric Shock
8.9.1 The guidance contained within the APEA/EI Blue Book for ‘PROTECTION AGAINST ELECTRIC SHOCK’ should be followed to ensure that the design of the AFI will mitigate the dangers of electric shock in any hazardous areas present. Outside of those areas the BS EN 7671 should be applied and the guidance of PG 03/09 & PG201 7/02 followed.
8.10 Electrical Earthing
8.10.1 Where an existing electrical installation is supplied from a TN-C-S system in which the neutral and protective functions are combined in part of the system to provide PME, stray currents passing through metalwork located in potentially hazardous areas may pose an increased risk of fire or explosion. Where the installation is supplied from a public low voltage network described as a TN-S system, the neutral and earth functions may not be separated throughout the system and may behave in a similar manner to a PME system and create similar risks.
8.10.2 For all new or refurbished AFI containing electrical equipment within a hazardous area an earthing facility derived from a shared supply over which the site has no control, shall not be used. Earthing arrangements for the installation should include the connection of the main earthing terminal to an earth derived from a dedicated TN-S or TT system. Further information can be located under ‘Earthing’ in the APEA/EI Blue Book and within EI MCoSP Part 1.
8.10.3 Provision should be made for the testing of individual electrodes, by separate radial connections to the main earthing bar. It may be necessary to install one or more independent electrodes for test purposes, depending on the electrode arrangement. Earthing arrangements should comply with the requirements of BS 7430.
8.10.4 A main earthing bar or terminal for an AFI with an electrical installation within a hazardous area should be provided as specified in the ‘Main earthing bar or terminal’ section of the APEA/EI Blue Book.
8.10.5 Earthing bars or terminals in equipment enclosures will follow the ‘Earthing bars or terminals in equipment enclosures’ section of the APEA/EI Blue Book.
8.10.6 Earthing of equipment located in hazardous areas will follow the ‘Earthing of equipment located in hazardous areas’ section of the APEA/EI Blue Book.
8.11 Conduit, ducting, pipes and trunking
8.11.1 For further information on installation and management of conduit, ducting, pipes and trunking see the ‘Conduit, ducting, pipes and trunking’ section of the APEA/EI Blue Book.
8.11.2 Electrical trunking and similar enclosures are not to pass through or beneath a hazardous area. Conduits entering or passing through hazardous areas should be installed in accordance with BS EN 60079-14 Clause 9.4.
8.11.3 Where ducting, pipes, trunking, access chambers or similar enclosures are used to accommodate cables, precautions should be taken to prevent the passage of flammable vapour or liquid from one hazardous zone to another zone, or to a non-hazardous area, and to prevent the collection of flammable vapour or liquid in such enclosures.
8.11.4 For further information on earthing of cable screening and armouring follow the ‘Earthing of
42

cable screening and armouring’ section of the APEA/EI Blue Book. Care should be taken to ensure that the earthing arrangements for data cable screening and armouring do not introduce potentially dangerous levels of energy into a hazardous area.
8.12 Bonding for electric shock and explosion protection
8.12.1 Electrical bonding of extraneous-conductive-parts and other supplementary bonding of metallic parts such as pipes, rails, steel framework etc, which do not form part of the electrical installation, should be undertaken as required by the ‘Bonding for electric shock and explosion protection’ section of the APEA/EI Blue Book.
8.12.2 In general, an electrical bond between two metallic parts may be achieved by a permanent and reliable metal-to-metal joint of negligible resistance. See the ‘Continuity of bonding conductors’ section of the APEA/EI Blue Book for further guidance.
8.13 Interconnection of earthing systems
8.13.1 Apart from local supplementary bonding, the electrical installation main earthing terminal and lightning protection, together with the metalwork or other non-electrical installations, should be connected together. See the ‘Interconnection of earthing systems’ section of the APEA/EI Blue Book for further guidance.
8.14 Electrical Wiring Systems
8.14.1 Within hazardous areas attention should be given to the requirements of the BS EN 60079 suite of standards, especially to the concepts of explosion protection. For areas other than hazardous areas, the relevant parts of this document and BS 7671 should be followed. Generally, the types of cable and the methods of their installation should comply with BS 7671. For further information see the ‘WIRING SYSTEMS’ section of the APEA/EI Blue Book.
8.14.2 Cable ties or clamps are not to be affixed to any type of cable support using self-adhesive fixings.
8.14.3 Duct systems notes below vary and are in addition to the requirements of the APEA/EI Blue Book:
- Ducts should be of such construction that they are not liable to be damaged by the drawing in or withdrawal of other cables,
- It should be noted that underground cable chambers, in hazardous areas may be zoned where a hazardous zone assessment shows that a hazard may exist. Any electrical equipment installed in the chamber must therefore be suitable for the zone in which it resides and If cable connection or termination boxes are installed in them, the boxes and any associated accessories (e.g. cable glands) must be ATEX certified for use within the zone in which it is installed and also be ingress protected to at least IP67 rating,
- To aid maintenance all cables, equipment and termination box’s will be permanently marked with engraved labels permanently fixed to these items and the details noted on the record drawings,
8.15 Electrical Labels and Warning Notices
8.15.1 For guidance see the ‘Labels and warning notices applicable to electrical installations’ section of the APEA/EI Blue Book. Note that some of the example signs identified will not be applicable to AFI.
43

8.16 Electrical Inspection and Testing
8.16.1 This Standard gives guidance on requirements for construction and major refurbishment of AFI electrical installations. Existing facilities which predate the modern electrical safety standards and industry codes of practice may therefore require allowances to be made to the requirements identified in this standard. Where required this should be agreed with DIO TS prior to construction beginning.
8.16.2 As part of the commissioning and testing of new or refurbished facilities containing hazardous areas the ‘INSPECTION AND TESTING’ section of the APEA/EI Blue Book can be used as guidance. The electrical installation within the hazardous area shall be inspected and tested in accordance with the requirements of BS EN 60079-14.
8.16.3 BS 7671 is intended to be generally applied to the electrical installation at an AFI. However other standards, Regulation and statutory requirements will also apply, for example, PG 03/09, PG 2017/02, BS EN 60079, MOD Defence Regulations and DSEAR. To satisfy the requirements of the Professional Inspector for AFI, MMOs are required to provide the appropriate electrical inspection and test documentation in hardcopy or via direct access to a suitably validated Computer Aided Facility Management (CAFM) system. Annex D of PG 2017/02 provides the model forms for petroleum facilities with hazardous areas.
8.16.4 Inspection and testing schedules for maintenance of an AFI are detailed in section 13 of this standard.
Design Approvals
9.1	A design approvals process should be specified in the contract to ensure that the requirements for approvals identified within this standard such as the installation of a buried tank are meet prior to the design moving onto construction.
Construction
10.1 General
10.1.1 Sound construction industry practice should be followed.
10.1.2 The project manager should ensure the Principal contractor addresses the following:
- A Construction programme should be provided prior to the start of work on site,
- The principal contractor will manage and coordinate the construction work of all contractors and sub-contractors to ensure efficient operation and site safety are maintained,
- They will ensure compliance with JSP 375,
- They will ensure construction is undertaken is a safe manner and the construction site is properly secured at all times,
- They will liaise with HoE representatives to ensure that the effects of the works on the operation of the wider site are minimised.
- They will ensure compliance with wider MOD procedures, such as flight line safety requirements,
- Ensure construction follows the design, obtain approvals for and document any changes to the design, ensure master design documentation is altered to reflect the
44

change and ensure it does not affect the safety, environmental protection and operation of the finished AFI.
- A management of change process should be adopted that ensures that any changes to the design made in construction are reflected in the design calculations and appropriate risk assessments etc.
- They will ensure all interested parties are given access to testing, commissioning and acceptance trails.
11.	Testing, Commissioning and Acceptance
11.1 Certificate of Fitness for Purpose
11.1.1 A Certificate of Fitness for Purpose (CFFP) represents formal confirmation by the project manager that new, or modified installations, are fit for purpose. A CFFP should be provided before first fill or use. This forms one of several requirements which shall be fulfilled to enable the Professional Inspector to provide a Certificate of Fitness for Continued Use for the installation.
11.1.2 The CFFP may be issued by the project manager, the Contractor or the MMO. It shall state that the AFI has been constructed, or modified, in conformance with the approved design and that it is fit for its intended purpose. The certificate shall be counter signed by;
- Project Manager,
- Principal Contractor,
- DFRMO Officer.
11.1.3 The Following processes should be completed prior to the issue of the CFFP. 11.2 Testing
11.2.1 Before any tank or pipework is brought into service it should be checked to confirm its integrity. Various methods may be used to fulfil this requirement. Correctly performed pressure and tightness tests are essential to ensure the quality of the installation and problem-free operation.
11.2.2 All tests should be fully documented including a clear indication of the scope, type and results of the tests. Copies of all such test certificates (including calibration certificates for test equipment) should be provided as part of the operation and maintenance manuals at handove r
11.2.3 Buried pipes shall undergo a mandatory tightness test prior to trench backfill. Both the primary and secondary pipe shall be tested in accordance with the manufacturer’s instructions to ensure there are no leaks in the system.
11.3 Verification Hazardous Areas
11.3.1 Verification is part of the commissioning procedure that should be carried out before the installation, or part of the site where changes have been made or new equipment has been installed, is brought into use. The purpose is to ensure the fire and explosion risks from potentially flammable atmospheres will be properly controlled.
11.3.2 Verification procedures are required by legislation (DSEAR) and in their entirety will also include consideration of the operational and work procedures, together with any emergency arrangements that are necessary to ensure the installed plant and equipment can be
45

operated correctly and safely. Verification carried out during commissioning should include the review of a list of measures required to ensure that:
- Records show that the storage tanks and all associated pipework have been pressure tested and are leak-tight,
- Leak detection systems for tanks and pipes are installed and operating correctly,
- A hazardous area classification drawing (if applicable) has been prepared and a visual inspection has been carried out to confirm that equipment is of the correct type and category for the zone where it is installed,
- For hazardous areas a verification dossier is compiled and held on site, as detailed within BS EN 60079-14,
- Equipment in the identified hazardous areas has been installed correctly and has been tested. All warning and information notices are in place,
- All electrical and other ducts from hazardous areas are properly sealed,
- Gauging and leak detection monitoring systems operate correctly,
- Drainage systems, including OWIs, are complete and tested,
- All emergency equipment has been installed and is in working order,
- The electrical installation has been completed and the relevant electrical certificate has been issued,
- The system is appropriate to all the fuels being stored,
- The environmental risk assessment has been properly undertaken.
11.3.3 Some of the verification checks can be carried out at an early stage, for example during the design, but others can only be carried out during commissioning. However, all the measures listed should have been installed before the first fuel delivery is permitted.
11.3.4 The MMO should ensure that a Competent Person carries out the verification. The MMO may be the Competent Person, but the help of others may also be needed, including the Designer, the installer of the equipment, test companies or an independent person or organisation. The person or persons involved shall have practical and theoretical knowledge of the fire and explosion hazards arising from hazardous areas, which may have been obtained from experience and/or professional training.
11.4 Commissioning
11.4.1 Commissioning of the ancillary installation is the Contractor’s responsibility. Where product (fuel) is required to commission the facility, the principal contractor will provide the project manager with sufficient notice of the volume and grade of product required to allow MOD to arrange delivery of the product to enable a timely start of commissioning.
11.4.2 Prior to receiving product, a CFFP shall be issued. Where applicable the AP (Petroleum) is to be provided with the commissioning procedure adopted by the Contractor and all relevant method statements and risk assessments to enable control under JSP 375 Volume 3 Chapter 5.
11.4.3 In addition to the measures listed in the verification procedure, the following elements should also be checked as part of the commissioning process prior to the first delivery of fuel;
- Where applicable all means of escape from buildings are clear, unobstructed and available for use,
- All tanks, fill points, vents and associated equipment are correctly marked and identified,
- Tightness testing of the complete drainage system, in accordance with BS EN 752, has been carried out certified as fit for purpose,
11.4.4 When the installation has received a delivery of fuel, the tank gauges, pump control systems,
46

all operating valves and components within the installation can be checked, adjusted and commissioned in accordance with the manufacturers' requirements to ensure correct and proper operation of the installation.
11.4.5 All operational level and alarm level sensors and controls must be proved end to end by adjustment of fuel levels and pressures prior to any testing using override facilities.
11.4.6 On completion of the commissioning activities, and prior to general use, there should be a final check for evidence of leaks from any equipment containing fuel. It should also be confirmed that all results and certificates from testing and commissioning operations are available and have been given to the DIO & MMO.
11.4.7 It is essential to maintain records of the results of initial tests and commissioning procedures for future reference. Copies of the records should be kept in a technical file as part of the handover manual and CDM procedures. They should also be retained electronically, together with other relevant documents for the AFI and these soft copies past to the DIO & MMO. By comparing these with future test results or other information (e.g. from maintenance work) it will be possible to identify any changes in the performance of the equipment, which may indicate a potential risk to safety or efficiency.
11.5 Handover
11.5.1 Once an installation has been commissioned and is considered ready for takeover by the OA, then as required by JSP 850 Part 2: Standards and Guidance ‘Acquire and Build’, ‘Siting and Handover Boards’ the original SB is to re-convene including a professional Inspector as a Handover Board (HB).
11.5.2 Two sets of Operation & Maintenance Manuals shall be supplied in hardcopy to the OA as well as a digital copy. In addition, one hard and one digital copy will go to the MMO and one digital copy to the DIO EFM. These should include:
- Original Equipment Manufacturer maintenance and operating manuals,
- Planned preventative maintenance details for the installation,
- List of spares required for the maintenance of the installation for a minimum period of 4 years of operation,
- List of all ATEX rated equipment complete with their certificates of conformity,
- As-built P&ID drawings,
- Electrical single line diagram drawings,
- Tank detail drawings,
- Site Plan/layout drawings,
- Construction drawings for bunds, plinths and drains etc,
- All Mechanical and Electrical Test and Installation Certifications,
- An Asset Register,
- Operating and installation instructions for equipment installed.
- All concept and detail design requirements.
- All DSEAR, Safety, Fire and Environmental Risk Assessments including any ancillary assessments made to support the safe operation of the installation.
47

12.	Decommissioning
12.1 General
12.1.1 All AFI which are to be taken out of use shall be made safe. The method will vary depending on the location of the asset, the product it has contained and whether it is to be temporarily or permanently decommissioned. For each specific project, all appropriate actions should be determined as part of the plan created from the activity detailed in JSP 317. If the site is to be disposed of DIO will advise in what state the AFI is to be handed over for disposal.
12.1.2 All decommissioning works undertaken within on AFI shall be undertaken in accordance with JSP 375 Volume 3 Chapter 5. Employers, the MMO and all Contractors have a legal obligation to ensure the work is carried out safely and that any equipment is left or maintained in a safe state.
12.1.3 The decommissioning activity shall commence as soon as practicable after the facility is taken out of service.
12.1.4 Decommissioning activities range from the complete closure and removal of an installation, to the replacement of individual tanks or lengths of pipe work. During decommissioning of installations, product could be lost to ground as a result of either deliberate or accidental release during dismantling and removal of the tanks and pipe work. In addition, a risk could arise off-site if contaminated tanks and pipe work are not disposed of in an appropriate manner. It is preferable to remove all permanently redundant tanks. If tanks are left in-situ, a risk could arise if any residual product remains in the tank as the integrity of the equipment would no longer be maintained or monitored. In general, the decommissioning shall include the following activities as a minimum;
- Completion of a risk assessment shall be undertaken by DIO and HoE staff. This shall include health and safety hazards to personnel, risks to the environment with a view to determining the decommissioning requirements,
- Disconnection and making safe any equipment to left in situ,
- Disconnection and removal of equipment not being retained on site,
- Collection, storage and safe removal of waste product from site,
- Any soil contamination encountered during removal of buried equipment should be assessed through a Land Quality Assessment (LQA). Refer to JSP850 and consult DIO EOLM SME (DIOTS-LQA@mod.gov.uk) for advice.
- Note that the Environmental Permit or Environmental Risk Assessment may specify that the tank and pipework be removed at the end of their working life.
12.1.5 The following subsections within this Standard set out the guidance to be followed for the main elements for an AFI. It is the intention that any site-specific issues are established within the risk assessment mentioned above and dealt with accordingly.
12.1.6 Those responsible for the decommissioning of the Installation should refer to the Public Health Act 1961 (or the Civic Government (Scotland) Act 1982), Dangerous Substances and Explosive Atmosphere Regulations 2002 and the accompanying L138 Dangerous Substances and Explosive Atmosphere Regulations – Approved Code of Practice, for statutory duties to be undertaken where the storage of flammable products has been stored and is no longer in use.
12.1.7 For each specific asset project, all appropriate actions will be determined as part of the plan created from the activity detailed in JSP317. The Contractor undertaking the decommissioning should be conversant with these recommendations, prior to commencing any works.
48

12.1.8 Where specialist activities are required, such as removal of hazardous waste, those responsible for the works shall use specialist Contractors with suitable documented experience.
12.2 Tank Decommissioning
12.2.1 A risk assessment is required that should consider health and safety and environmental risks to determine if tanks are to remain in situ or be uplifted and removed from site.
12.2.2 Where the tank is to be transported by road the requirements of ADR must be considered see https://www.hse.gov.uk/cdg/commonproblems/tanks.htm for guidance. Note that a gas free certificate may be required to allow the transportation of the tank.
12.2.3 A specialist Contractor should be used for the uplifting and removal of tanks. The Contractor shall be fully informed of all potential hazards prior to undertaking the works. No work should be started prior to the production of a risk assessment which should cover as a minimum the lifting operation, any dismantling or cutting of the tank, cleaning and shot blasting of steelwork and removal of the tank. All lifts will comply with The Lifting Operations and Lifting Equipment Regulations 1998.
12.2.4 For the purposes of this Standard the Contractor undertaking the decommissioning is to assume that ground surrounding the tank is likely to have been contaminated with the product stored in the tank, more so where the tank is buried. Where evidence suggests that product has contaminated the surrounding ground, the Contractor shall have the suspected area investigated by a Competent Person with a view to dealing with contaminant in accordance with local legislation. Further guidance on this issue is provided in BS 6187 ‘Code of practice for full and partial demolition’. See above serial 12.1.4.
12.2.5 Prior to any work being carried out on the tank, or entry into the tank, the tank shall be made safe by having all residual fuel removed as far as reasonably practicable. This is referred to as ‘bottoming’. All associated pipework attached to the tank should have all residual fuel drained back to the tank before bottoming can be undertaken. Tank vents should be detached and dismantled. The Contractor shall use a specialist Contractor for safe disposal of waste product from site.
12.2.6 Only in the most extreme circumstances, and where there is no alternate method of work, should entry into a tank be permitted. The final decision for tank entry lies with the AP (PET). If entry to the tank is required, then reference shall be made to Confined Spaces Regulations and carried out in accordance with JSP 375 Volume 3 Chapter 5.
12.2.7 On completion of the tasks described above and where required by the grade of the product that was stored in the tank, then it should be made inert to remove the risk of explosion. The following options may be considered to achieve this;
- Fill the tank with an inert substance (water, hydrophobic foam or nitrogen foam),
- Fill the tank with inert gas (Nitrogen, dry ice, combustion gas) - recommended for above ground tanks prior to a permanent process being applied,
- Clean and degas tank prior to a permanent process being applied.
12.2.8 When filling the tank with an inert substance or gas it shall be assumed that explosive vapours will be displaced through the opening of the tank creating an explosive atmosphere. The Contractor responsible for the decommissioning shall ensure that the extent of any hazardous area is minimised and take all precautions under DSEAR to remove any possible sources of ignition.
49

12.3 Aboveground Tanks
12.3.1 A decision on the future of aboveground tanks that are permanently taken out of service shall be taken at the earliest opportunity in line with extant Government guidance.
12.4 Buried Tanks
12.4.1 Government guidance for Underground Storage Tanks (UST) should be followed. https://www.gov.uk/guidance/prevent-groundwater-pollution-from-underground-fuel-storage-tanks/decommissioning-an-underground-storage-tank.
12.4.2 The preference is that all buried tanks when permanently out of use shall be removed from site to remove the risk of any future environmental hazards. However, it is recognised that there may be scenarios where the tank is to be decommissioned and left in situ.
12.4.3 Prior to excavating and lifting the tank, the water table level should be investigated to determine the likelihood of the tank moving during its removal. This may have a bearing on the Contractor’s choice of whether to fill the tank with foam or water as the density of foam is such that the tank may float when the holding down straps are released.
12.4.4 The tank should not be lifted by chains or wire ropes as the potential of sparking exists, only fabric lifting straps should be used. The APEA/EI Blue Book provides detailed guidance on the removal of underground tanks however attention is given to the following precautions;
- The tank shall be disconnected from all attached pipework,
- All tank openings sealed to prevent escape of inerting gas or liquid. This includes any holes to tank structure caused by corrosion,
- A suitable pressure relief valve should be fitted to the tank.
12.4.5 Where tanks are to be made safe and left in situ then tasks identified in section 12.2.5 shall be completed in the first instance to remove the potential explosive atmosphere within the tank. It is then recommended that the tank is filled by one of the following three options.
- Sand and cement slurry,
- Hydrophobic foam,
- Foamed concrete.
Refer to the 4th Edition APEA/EI Blue Book section 12.2.4 for detailed procedures relating
to the tank filling methods above.
12.5 Pipework
12.5.1 The removal of pipework should be carried out prior to the removal of the tank, it should not be carried out until fuel has been drained back to the tank and it has been isolated from sources of fuel and from the site earth bonding arrangements. A flammable atmosphere or residual product may be present in pipework and a precautionary measure of flushing with water should precede the removal and dismantling work, which should be accomplished by cold work only.
12.5.2 Excavated pipework should be removed from the installation as soon as possible and disposed of safely. Care should be taken to ensure that no fuel or water contaminated with fuel is released into the ground or allowed to enter any drainage system or watercourse. Water used to flush out the pipework should be collected for safe disposal. It may be possible, with appropriate approval, to discharge this water through the OWI. Refer to site permitting requirements via project Aquatrine where they are responsible for the OWI.
50

12.6 OWI and Drainage
12.6.1 Where the OWI will serve no useful purpose in connection with any intended future use of the site, it should, wherever practicable, be uplifted and removed from site for safe disposal. Alternatively, the OWI chamber(s) should be filled, in situ, with concrete slurry, sand or other similar inert material Refer to Project Aquatrine for advice where they are responsible for the OWI.
12.6.2 Before removing or infilling the OWI and with the assistance of project Aquatrine where required, it is necessary to carry out the following preparatory work, prior to any of these actions;
- Arrangement should be made for a hazardous waste disposal contractor to remove any liquid or sludge contained in the chambers,
- All inlets to any associated redundant drainage system should be sealed off,
- The outlet pipe from the redundant OWI should be sealed and capped off at the point where it connects to any remaining live drainage system within the site. Where the surface drainage is to remain operational the inlet and outlet pipes to the OWI should be linked.
12.7 Electrical Installation
12.7.1 Where the installation is to be totally decommissioned and demolished, the Electrical AP should be requested to disconnect the supply to the installation prior to the commencement of the decommissioning work.
13.	Periodic Inspection and Maintenance Schedules and Frequencies 13.1 General
13.1.1 The following FDIS SFG20 Schedules list the required maintenance tasks for each element of an AFI and the frequency of which the tasks shall be undertaken. The inclusion of these activities, within the facilities maintenance regime are intended to maintain the facility such that it is fit for purpose, safe to operate, and to achieve the desired operational design life.
13.1.2 It is not the intention of this Standard to provide instruction on how to undertake these tasks, however, it is expected that those responsible for completing the inspection and maintenance activities will be competent to do so.
13.1.3 All inspection and maintenance tasks carried out on AFI shall be recorded and made available to any permitting/licencing authority or Professional Inspector that requires to see them.
13.2 Fuel Quality
13.2.1 The need for fuel quality checking should be determined by risk assessment. The following issues should be considered:
- How essential is the fuel using equipment? i.e. heating boiler for a none essential office may be considered of low importance whilst a standby generator for a hospital of high importance,
- How regularly is the fuel turned over? The heating boiler with a small tank uses the volume of the tank contents every month so is at low risk of in tank microbial
growth, The standby generator has a large tank and very low turnover so growth in the tank could happen without anybody even noticing,
51

- How good is your fuel supply? Are your supplies from various low-quality suppliers or from a reliable high-quality supplier, consider the likelihood of contaminated supply containing microbial growth or excess water etc,
- Will the tank be kept full? A large tank with a little fuel in it offers a large area tank surface and space above the fuel in which condensation can form and add water to the fuel.
- What are the ambient conditions? High humidity and lots of condensation can add water to the fuel whilst low humidity and little condensation may see no appreciable difference,
- How much biofuel is in the product used? What are its properties? Generally, the higher the content of bio fuel the more problems you will have with contamination by microbial growth and water contamination as biofuels tend to be hydroscopic to a much greater extent than petrochemical fuels.
13.2.2 Where it is determined that testing is required then it should meet the requirements of the generator engine manufacturer or if not specified as a minimum, water contamination to be within the limits of the relevant standard for the fuel and particle content coding value of 18/16/13 from the ACEA Worldwide Fuel Charter fuel standard to reporting sizes of 4,6 & 14 micron as per BS ISO 4406.
13.2.3 JSP 317 has guidance on fuel quality standards and testing frequency and whilst not primarily aimed at ancillary tank installations the guidance on ground fuels provides a sound basis on which to base the type of test required and testing frequency required see JSP 317 Pt 2, Vol 3 (v6.4 Apr 20) Annex L – The Frequency of Testing for Fuels Held in Bulk (Permanent, Non-permanent and mobile) Storage, Table 2.3.1.L.2 – Frequency for testing Ground Fuels.
13.2.4 All fuels will eventually degrade so tanks where fuel turnover is very low i.e. the bulk stays in place for 5 years may require additional fuel to be added to ‘freshen’ the tank, where this is a concern the fuel supplier should be approached to agree the best option for testing and if required the adding of treatments to the fuel to maintain its condition.
13.2.5 For AFI without fuel polishing equipment the following might be expected:
- Standby generator bulk storage tank with minimal usage every 12 months using petrochemical BS 2869 A2 diesel, this would align reasonably with a fuel that was not used for at least 12 months in JSP 317 and hence would require testing every 12 months.
- In a humid environment with a questionable fuel supply in the same standby generator installation you may assess the need for a test every 6 or even 3 months until some assurance was gained over fuel quality
- A small tank feeding a boiler with high fuel turnover using a tank a month with the same petrochemical BS 2869 A2 diesel would likely require no testing at all.
13.2.6 For AFI with fuel polishing equipment the following might be expected:
- Standby generator bulk storage tank with minimal usage every 12 months using BS 2869 A2 diesel, assuming regular polishing. You may well assess the need for an initial test at 12 months then set a future testing schedule based on the residue recovered from the filters of the polishing unit and the fuel quality test results.
- For the same installation as above but that required changing or cleaning of filters within the 12 months between tests increased testing may be sensible.
- Where the polishing unit has been fitted due to the fuel supply being of low quality even when fuel turnover is high but where filter blocking is a regular issue you may wish to undertake monthly test to identify if fuel quality was improving or otherwise.
52

13.3 Repairs and Modifications
13.3.1 It is not intended that an existing AFI should be brought into line with the most recent standards during routine maintenance and repair works. Where the repairs made amount to modification of the original then the works shall comply with the guidance provided within this Standard. Modification of equipment or change to design shall only be permitted where a review against this standard has first been undertaken that indicates an improvement towards or compliance with this standard such that any change to the current facility shall in no way increase the risk to the user or the environment.
13.3.2 A Management of Change process will be implemented and maintained to document any changes made to the installation.
13.3.3 All repair and modifications shall be undertaken by Competent Persons and/or suitable qualified contractors.
53

13.4 Periodic Inspection and Maintenance Schedules for AFI
13.4.1 Maintenance of AFI’s should be undertaken in line with the tasks contained within the MOD FDIS contract SFG20 Schedules.
13.4.2 The MMO should ensure that the SFG20 Schedules in use encompass the manufacturers recommendations and instructions for the equipment being maintained. Where this results in conflict between the manufacturers requirements and the SFG20 Schedule the issue should be addressed to DIO-TS.
13.4.3 Where it appears more than one schedule may be applicable DIO-TS should be consulted to obtain agreement to the use of the schedule that it is proposed will be implemented.
13.4.4 Hardstanding containment requirements are covered within this standard, however the physical maintenance of the hardstanding and buildings structures is not covered by this standard. The maintenance of the hardstanding and building fabric should be encompassed within the estate wide maintenance as it is considered they are not likely suffer any additional wear and tear over and above that of any other general area.
13.4.5 Existing facilities which predate the modern electrical safety standards and industry codes of practice may require allowances to be made to the maintenance requirements identified in this standard. Where required this should be agreed with DIO TS prior to the SFG20 schedule being amended.
13.4.6 Electrical equipment associated with Class III only AFI’s should be inspected on a 3-year rolling schedule, as per the below guide:
YEAR		GRADE	PROPORTION
1		Visual	100% of Equipment
2		Close	100% of Equipment
3		Detailed	100% of Equipment

This table should be used in preference to the one in SFG20 Schedule 1120-16*
13.4.7 The table below is indicative of the schedules likely to be required for an average AFI, but each installation must be assessed to ensure that all applicable SFG20 Schedules have been implemented. Frequencies will be as specified within the schedule.
Schedule number and description.	Class III	Class III	Kerosene based
	products	products	products (always
	without a	with a	have a DSEAR
	DSEAR	DSEAR	hazardous area)
	hazardous	hazardous	excepting domestic
	area.	area.	installations.
14-02 Electrical Services (excluding Electrical Controllers and Pneumatic Relays)	X
14-14 Level Controllers	X
14-21 Instrument Control Panel	X
36-04 External Lighting including Illuminated Signs	X	X	X
38-01 Lightning Conductor and Earth	X
39-01 Motors - Drive Elements	X
40-01 Pipework In General	X	X	X
40-02 Pipework Systems - Mountings	X	X	X

54

40-10 Pipework for Low Pressure Natural Gas, Liquefied Petroleum Gas (LPG) or Oil	X	X	X
40-19 Free Fall Fire Valves - Gas and Oil	X	X	X
40-22 Solenoid Gas/Oil Shut-off (Safety) Valves	X	X	X
44-04 Armoured Cables and Conduits	X
44-06 LV Earthing	X
44-07 Distribution Boards	X
44-08 Electrical Installation - Generally	X
44-09 Three Phase Circuits	X
44-10 Isolators/Starters/Fuse Switches	X
44-11 Periodic Inspection and Testing	X
45-15 Fuel Oil Transfer Pumps	X	X	X
48-03 Separator Systems for Light Oils - Petrol and Oil	X	X	X
50-14 Magnetic Level Sensors/Switch	X	?	?
50-16 Float Switch	X	?	?
55-01 Starters - Drive Elements	X
55-02 Starters - Star Delta	X
56-05 Oil Storage Tanks - Above Ground	X	X	X
56-06 Oil Storage Tanks - Underground	X	X	X
58-01 On/Off Switching Devices	X
58-02 Control Relays	X
62-06 Pressure Control Valves	X	X
87-16 Meter Reading/Tank Dip - Oil	X	X
87-18 Oil Storage Tanks - Above Ground	X	X
1120-05 Professional inspection of fuel infrastructure and flammable dangerous goods stores.	X	X	X
1120-11 Tank Ancillary and Monitoring Equipment - bulk fuel installations			X
1120-12 Environmental Containment - bulk fuel installations	X	X	X
1120-16 Electrical Equipment - bulk fuel installations*		X	X
1180-02 Lightning Protection System (Hazardous areas - Petroleum Facilities)		X	X
1250-02 Roads, hardstandings, paved areas, footpaths	X	X	X

55

14.	Technical Authority
14.1 General
14.1.1 MOD Technical Authority is vested in Head of Engineering, DIO Technical Services. Technical advice and assistance on AFI matters can be obtained from DIO. Approaches may be made through local DIO offices or directly to:
Matthew Spare BEng MSc CEng MIMechE
Principal Mechanical Engineer (Mechanical and Fuel Infrastructure)
Technical Services
Defence Infrastructure Organisation
St George’s House
Defence Infrastructure Organisation Head Office
DMS Whittington
Lichfield
Staffordshire
WS14 9PY.
Email: matthew.spare101@mod.gov.uk
14.1.2 This Standard have been devised for the use by the Crown and its Contractors in the execution of contracts for the Crown and, subject to the Unfair Contracts Terms Act 1977, the Crown shall not be liable in any way whatever (including but without limited negligence on the part of the Crown its servants or agents) where the specification is used for other purposes.
56