## Explanation
Situation
Over a 24 month period represented by a target period, a CCA facility required 3,600,000 kWh of steam and 1,680,000 kWh of delivered (metered) electricity to produce 120,000 tonnes of product.
The site has a natural gas fired CHP which normally supplies all of the site’s heat demand. The electricity generated by this CHP also normally satisfies all of the site’s electricity demand, with some electricity generated spilled to the grid.
The site carries out routine maintenance of the CHP at the same time as the annual 2 week site maintenance shut down. CHP down time for maintenance is therefore predictable and planned and does not occur at the same time as the site is producing output.
However, during the second 12 months of the target period there was a failure of the CHP’s prime mover, putting the CHP out of action for 3 months, which did not include the routine site 2 week shutdown. The site was required to continue producing as normal over this 3 month period. In order to satisfy the electricity and steam demand of production during this 3 month period, the site was required to import electricity from the grid and burn gas in its back-up boilers.
This means that:
· Over months 1-13 and 17-24 the site operated normally, derived all of its steam and electricity requirements from the on-site CHP and exported some surplus electricity to the grid.
· Over months 14-16 the site had to continue operating without the CHP and instead had to import electricity from the grid and burn gas in its back-up boilers in order to satisfy its electricity and heat requirements.
Data Required for evaluation of supply disruption effect
The CCA Facility’s demand for delivered electricity and steam and its production over the normal periods of Month 1-13 and 17-24 are highlighted in ORANGE (B2:N5, R2:Y5).
The CCA Facility’s demand for delivered electricity and steam and its production over the period when the CHP was not running are highlighted Purple (P4:R6).
The primary electricity imports from the grid and gas burned in the back-up boilers to satisfy the site’s demand for delivered electricity and steam when the CHP was not operating are highlighted BLUE (O7:R8).
The performance characteristics of the CHP over the period it was operating normally are highlighted GREEN (c11:N16, s11:z16).
Figures in italics in the Range B17:N30, R17:Y30 are calculations using the CHP algorithm necessary to apportion CHP fuel to CHP generated electricity and heat and to calculate the heat credit in respect of CHP electricity exports to the grid.
Is Supply Disruption Relevant?
Supply Disruption is relevant only if the Target Unit has failed to meet its target. In this example we have:
Actual Target = 53.000 kWh
Actual Performance = 54.337 kWh/tonne
The Target Unit has failed its target and so can go through the process of demonstrating that the supply disruption was responsible of it failing to meet its target.
Determination of 'Normal' operation data
The solution is to calculate the amount of primary energy the CCA facility would have had to report for the 24 month period if the CHP had not experienced an unexpected failure for the 3 month period and then compare this against the amount of primary energy the CCA facility actually had to report for the 24 month period.
STEP 1 Determine the average heat to power ratio of the CHP over the period of normal operation. This is the sum of heat generated by the CHP over months 1-13 and 17-24 divided by the power generated by the CHP over the months 1-13 and 17-24.
STEP 2 Determine the average efficiency of the CHP over the period of normal operation. This is the sum of total heat generated by the CHP over months 1-13 and 17-24 and total power generated by the CHP over the months 1-13 and 17-24 all divided by the total fuel consumed by the CHP over the months 1-13 and 17-24.
STEP 3 Determine the demand for steam in the period of the CHP failure (months 14-16). This is the metered steam consumption for this period .
STEP 4 Determine the quantity of electricity that the CHP would have generated in month 14-16 if the CHP satisfied this demand for steam. This is the quantity of steam demanded over month 14-16 divided by the average heat to power ratio over month 1-13 and 17-24 (STEP 1).
STEP 5 Determine the quantity of CHP generated power that would have been surplus to requirements over month 14-16. This is CHP power generated over month 14-16 minus the delivered electricity demand over month 14-16. The result is the CHP power generated over month 14-16 that would have been exported to the grid.
STEP 6 Calculate the heat credit arising from the CHP electricity that would have been exported to the grid over month 14-16
STEP 7 Calculate the fuel associated with the CHP electricity the CCA facility would have consumed over month 14-16
STEP 8 Calculate the fuel associated with the CHP heat the CCA facility would have consumed over month 14-16.
STEP 9 Calculate the heat credit that would have applied to the CCA facility in respect of the CHP heat it would have consumed over month 14-16. (The CCA facility gets all the heat credit in this case because it consumed all of the CHP heat outputs).
STEP 10 Calculate the total implied primary energy that the CCA facility would have reported in month 14-16 if the CHP was operating normally.
Revision of target performance
STEP 11 Determine the actual CCA facility primary reportable energy over the period months 1-14 and 17-24.
STEP 12 Determine the actual primary energy consumption of the CCA facility over the period month 14-16.
STEP 13 Calculate the additional reportable primary energy arising as a result of the unexpected failure of the CHP. This is (STEP 11 + STEP 12) – (STEP11 + STEP 10). This is used in the target calculator.

## CHP Shutdown Example
DATA REQUIRED FOR EVALUATION OF SUPPLY DISRUPTION EFFECT
CCA Facility Production and Delivered Energy Consumption over 24 months
Month | Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Production (tonne) | 120000 | 5000 | 4500 | 4700 | 4650 | 5500 | 5300 | 5350 | 4500 | 4700 | 4650 | 5500 | 5300 | 5350 | 4500 | 4700 | 4650 | 5500 | 4500 | 4700 | 4650 | 5500 | 5650 | 5650 | 5000
Delivered Electricity Demand (kWh) | 1680000 | 70000 | 63000 | 65800 | 65100 | 77000 | 74200 | 74900 | 63000 | 65800 | 65100 | 77000 | 74200 | 74900 | 63000 | 65800 | 65100 | 77000 | 63000 | 65800 | 65100 | 77000 | 79100 | 79100 | 70000
Steam Demand (kWh) | 3600000 | 150000 | 135000 | 141000 | 139500 | 165000 | 159000 | 160500 | 135000 | 141000 | 139500 | 165000 | 159000 | 160500 | 135000 | 141000 | 139500 | 165000 | 135000 | 141000 | 139500 | 165000 | 169500 | 169500 | 150000
Primary Electricity Imported from Grid (kWh) |  | 14: 163800; 15: 171080; 16: 169260
Gas Consumed in Back-up Boilers (kWh) |  | 14: 168750; 15: 176250; 16: 174375
CHP Fuel Consumption, Electricity and Heat Generation (Normal CHP Operation)
Month | Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
CHP Fuel (kWh) | 6631047.4776 | 316540.568 | 314494.8272 | 311526.0069 | 298862.5329 | 335071.2197 | 341566.7787 | 304361.5676 | 257306.2262 | 286764.7059 | 297668.0384 | 314229.0964 | 313843.2233 | 305520.3046 | NO CHP OPERATION |  |  | 368866.7642 | 278156.5919 | 280320.0889 | 300749.4354 | 344509.6191 | 381128.8234 | 355300.9201 | 324260.1388
CHP Elec Generated (kWh) | 1809103.1201 | 75376.8844 | 87662.3377 | 87037.037 | 78370.7865 | 90659.3407 | 101273.8854 | 80250 | 67500 | 88125 | 77500 | 84183.6735 | 85483.871 | 81472.0812 |  |  |  | 97633.1361 | 75842.6966 | 78770.9497 | 91776.3158 | 105095.5414 | 107961.7834 | 85606.0606 | 81521.7391
CHP Heat Generated (kWh) | 3184500 | 150000 | 135000 | 141000 | 139500 | 165000 | 159000 | 160500 | 135000 | 141000 | 139500 | 165000 | 159000 | 160500 |  |  |  | 165000 | 135000 | 141000 | 139500 | 165000 | 169500 | 169500 | 150000
CHP Efficiency (%) | 15.843 | 71.2% | 70.8% | 73.2% | 72.9% | 76.3% | 76.2% | 79.1% | 78.7% | 79.9% | 72.9% | 79.3% | 77.9% | 79.2% |  |  |  | 71.2% | 75.8% | 78.4% | 76.9% | 78.4% | 72.8% | 71.8% | 71.4%
H:P |  | 1.99 | 1.54 | 1.62 | 1.78 | 1.82 | 1.57 | 2 | 2 | 1.6 | 1.8 | 1.96 | 1.86 | 1.97 |  |  |  | 1.69 | 1.78 | 1.79 | 1.52 | 1.57 | 1.57 | 1.98 | 1.84
Apportionment of CHP Fuel
Month | Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
CHP Fuel for Electricity (kWh) | 3525273.7511 | 158666.9514 | 177680.6933 | 172113.816 | 158128.3243 | 175429.958 | 191353.9376 | 152180.7838 | 128653.1131 | 159313.7255 | 156667.3886 | 158701.5639 | 162613.0691 | 153914.5111 | NO CHP OPERATION |  |  | 199927.7855 | 147172.7999 | 147926.1683 | 170880.361 | 193002.5878 | 213517.5481 | 178543.1759 | 168885.489
CHP Fuel for Heat (kWh) | 3105773.7265 | 157873.6166 | 136814.1339 | 139412.1909 | 140734.2086 | 159641.2618 | 150212.841 | 152180.7838 | 128653.1131 | 127450.9804 | 141000.6498 | 155527.5326 | 151230.1542 | 151605.7935 |  |  |  | 168938.9787 | 130983.7919 | 132393.9206 | 129869.0744 | 151507.0314 | 167611.2753 | 176757.7442 | 155374.6499
Total CHP Fuel (kWh) | 6631047.4776 | 316540.568 | 314494.8272 | 311526.0069 | 298862.5329 | 335071.2197 | 341566.7787 | 304361.5676 | 257306.2262 | 286764.7059 | 297668.0384 | 314229.0964 | 313843.2233 | 305520.3046 |  |  |  | 368866.7642 | 278156.5919 | 280320.0889 | 300749.4354 | 344509.6191 | 381128.8234 | 355300.9201 | 324260.1388
Heat Credit
Month | Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
CHP Electricity Export to Grid | 323003.1201 | 5376.8844 | 24662.3377 | 21237.037 | 13270.7865 | 13659.3407 | 27073.8854 | 5350 | 4500 | 22325 | 12400 | 7183.6735 | 11283.871 | 6572.0812 | NO CHP OPERATION |  |  | 20633.1361 | 12842.6966 | 12970.9497 | 26676.3158 | 28095.5414 | 28861.7834 | 6506.0606 | 11521.7391
CHP Fuel for Electricity Exported to Grid | 626551.6064 | 11318.2425 | 49987.5017 | 41995.7711 | 26776.3962 | 26431.447 | 51155.286 | 10145.3856 | 8576.8742 | 40359.4771 | 25066.7822 | 13542.5334 | 21464.9251 | 12415.7706 |  |  |  | 42251.4053 | 24921.2608 | 24358.509 | 49669.2249 | 51596.0251 | 57080.3579 | 13569.2814 | 23869.1491
Primary Energy of Grid Equivalent | 839808.1123 | 13979.8995 | 64122.0779 | 55216.2963 | 34504.0449 | 35514.2857 | 70392.1019 | 13910 | 11700 | 58045 | 32240 | 18677.551 | 29338.0645 | 17087.4112 |  |  |  | 53646.1538 | 33391.0112 | 33724.4693 | 69358.4211 | 73048.4076 | 75040.6369 | 16915.7576 | 29956.5217
Primary Energy Saving/Heat Credit | 213256.5059 | 2661.657 | 14134.5762 | 13220.5252 | 7727.6487 | 9082.8387 | 19236.8159 | 3764.6144 | 3123.1258 | 17685.5229 | 7173.2178 | 5135.0176 | 7873.1394 | 4671.6406 |  |  |  | 11394.7485 | 8469.7504 | 9365.9602 | 19689.1961 | 21452.3825 | 17960.2791 | 3346.4762 | 6087.3726
CCA Facility Primary Energy Consumption
Month | Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
CCA Facility Fuel for CHP Electricity | 3654338.3973 | 147348.7089 | 127693.1916 | 130118.0449 | 131351.9281 | 148998.511 | 140198.6516 | 142035.3982 | 120076.2389 | 118954.2484 | 131600.6065 | 145159.0304 | 141148.144 | 141498.7406 | 755616.2526 |  |  | 157676.3801 | 122251.5391 | 123567.6593 | 121211.1361 | 141406.5626 | 156437.1903 | 164973.8945 | 145016.3399
CCA Facility Fuel for CHP Heat | 3105773.7265 | 157873.6166 | 136814.1339 | 139412.1909 | 140734.2086 | 159641.2618 | 150212.841 | 152180.7838 | 128653.1131 | 127450.9804 | 141000.6498 | 155527.5326 | 151230.1542 | 151605.7935 |  |  |  | 168938.9787 | 130983.7919 | 132393.9206 | 129869.0744 | 151507.0314 | 167611.2753 | 176757.7442 | 155374.6499
Heat Credit for Grid Export | 213256.5059 | 2661.657 | 14134.5762 | 13220.5252 | 7727.6487 | 9082.8387 | 19236.8159 | 3764.6144 | 3123.1258 | 17685.5229 | 7173.2178 | 5135.0176 | 7873.1394 | 4671.6406 |  |  |  | 11394.7485 | 8469.7504 | 9365.9602 | 19689.1961 | 21452.3825 | 17960.2791 | 3346.4762 | 6087.3726
CCA Facility Primary Energy to Report from CHP Consumption | 6814754.3653 | 302560.6685 | 250372.7493 | 256309.7106 | 264358.488 | 299556.934 | 271174.6768 | 290451.5676 | 245606.2262 | 228719.7059 | 265428.0384 | 295551.5454 | 284505.1588 | 288432.8934 |  |  |  | 315220.6103 | 244765.5806 | 246595.6197 | 231391.0143 | 271461.2115 | 306088.1865 | 338385.1625 | 294303.6171
Primary Electricity Imported from Grid (kWh) |  | 14: 163800; 15: 171080; 16: 169260
Gas Consumed in Back-up Boilers (kWh) |  | 14: 168750; 15: 176250; 16: 174375
Actual Performance | 56.7896
IS SUPPLY DISRUPTION RELEVANT?
Target (kWh/tonne) | 53
Actual Performance (kWh/tonne) | 54.3371
Can supply disruption be invoked? | YES
DETERMINATION OF 'NORMAL' OPERATION DATA
For Months 1-13 and 17-24 (Normal CHP Operation)
STEP 1 CHP Average Heat to Power Ratio | 1.7603
STEP 2 CHP Average CHP Efficiency | 75.31%
Applying Normal CHP Operation to Months 14-16
STEP 3 Demand for Heat | 415500
STEP 4 Implied CHP power generation | 236044.0717
STEP 5 Actual Demend for Electricity | 193900
STEP 5 Implied Export to the Grid | 42144.0717
Implied CHP Fuel | 865190.8391
Implied CHP Fuel for Electricity | 460175.5217
Implied CHP Fuel for Heat | 405015.3174
STEP 6 CHP Fuel for Implied Export to the Grid | 82161.2254
STEP 6 Primary Energy of Grid Equivalent | 109574.5865
STEP 6 Primary Energy Saving/Heat Credit | 27413.361
STEP 6 Heat Credit for Grid Export | 27413.361
Implied CHP Primary Energy for CCA Facility for Months 14-16
STEP 7 CCA Facility Fuel for CHP Electricity | 378014.2962
STEP 8 CCA Facility Fuel for CHP Heat | 405015.3174
STEP 9 Heat Credit for Grid Export | 27413.361
STEP 10 Total Implied CCA Facility Primary Energy for Months 14-16 | 755616.2526
REVISION OF TARGET PERFORMANCE
STEP 11 Actual CCA Facility Consumption for Months 1-13 and 17-24 | 6295379.3653
STEP 12 Actual CCA Facility Consumption for Months 14-16 | 1023515
STEP 13 Additional Energy Incurred as a Result of Supply Disruption | 267898.7474