###### FUEL & GAS SAFETY ASSURANCE ASSESSMENT (FGSAA)

Advice and guidance on completion of this assessment should be sought from the FGSR; however in the first instance Units are encouraged to review the referenced publications and discuss issues with their TLBs.

For Army HQ, completion of this assessment will be conducted on the Unit’s behalf by the Army HQ Petroleum Inspectorate. This will be undertaken in conjunction with the annual Specialist Petroleum Inspection (SPI), which the FGSR will use as assurance and reference during Regulatory Visits. In this instance, Army HQ Inspectors should seek guidance from FGSR as required.

Completed reports should be emailed to DSA-DLSR-FGSR Insp Group@mod.uk, via your TLB. FGSR will aim to process the report within 6 weeks of the receipt date. Further guidance can be sought from the persons listed below.
FGSR Contacts:

FGSR SO1	DSA-DLSR-FGSR@mod.uk	9679 83803
FGSR SO2	DSA-DLSR-FGSR-SO2@mod.uk	9679 83804
FGSR Inspector 1	DSA-DLSR-FGSR-Insp1@mod.uk	9679 83798
FGSR Inspector 1a	DSA-DLSR-FGSR-Insp1a@mod.uk	9679 83796
FGSR Inspector 2	DSA-DLSR-FGSR-Insp2@mod.uk	9679 83800
FGSR Inspector 2a	DSA-DLSR-FGSR-Insp2a@mod.uk	9679 83801
FGSR Compliance	DSA-DLSR-FGSR-Compliance@mod.uk	9679 83802
FGSR Gas	DSA-DLSR-FGSR-Gas@mod.uk	9679 83797

The details highlighted in red in the table below must be completed for the assessment to be processed by FGSR.
Assessment Type:
Unit:					UIN:
Bks/Stn:
Address:
BFPO No./Postcode:					Received / Completed by: (Name/Rank)
Date FSAA received:					Date FGSR informed:					Date to be complete by:
Type(s) of Installation:
Unit Key Personalities
Appointment					Name/Rank				Tel No.				DII (F)/ Email Address
TLB
Operational Duty Holder (2*)
Delivery Duty Holder
Head of Establishment
Delegated Operating Authority (if delegated by HoE)
OC Fuels
F&L Manager
DIO Representative
MMO Representative
Unit SHE/SHEF
2nd Party Assurance Inspector (if applicable)
Remarks:
Date Returned:					Returned by:					Signature:

Introduction

1.	The FGSAA has been produced to enable units to conduct self-assessment of their fuel infrastructure and provide assurance to the FGSR, and their TLB. The output of this process being the safe storage and handling of fuels and lubricants across the MoD estate.

As the Operating Authority, the Head of Establishment (HoE) should formally delegate the task of completing this document. Assistance of additional key personalities and Subject Matter Experts (SME) will be essential when interpreting and completing this assessment.

3.	Each applicable section should be answered honestly with no fear of retribution. It should be stressed to personnel at all levels, that accurate reporting is vital to the success of self-assessment and that all assessments should be completed accurately and honestly. Fuel safety reporting must take on a proactive approach and all MoD staff must promote a positive safety culture. By completing a self-assessment inaccurately, the unit could face further enforcement action.

4.	All units will be externally audited by FGSR on a 1, 3 or 5 year basis, depending on the risk associated with the site.

Useful Reference Documents:

- APEA/IP Design, Construction, Mod, Maintenance and Decommissioning of Filling Stations.
- Control of Pollution (Oil Storage) Regulations 2001
- DIO Practitioners Guide PG 05/12
- DIO Practitioners Guide PG 06/12
- Def Stan 01-5
- Def Stan 05-52
- DMG 14 Mechanical Transport Fuelling Installations (MTFI)
- EA PPG 2 – Document withdrawn by the EA, but still available. Content remains useful.
- EA PPG 3 – Document withdrawn by the EA, but still available. Content remains useful.
- EA PPG 7 – Document withdrawn by the EA, but still available. Content remains useful.
- BSI 858 – Separator Systems for Light Liquids (e.g. Oil and Petrol)
- UKLPG COP 1 Part 1, Bulk LPG Storage Installations at Fixed Installations – Design, Installation & Operations of Vessels Located Above Ground.
- UKLPG COP 7, Storage of Full & Empty LPG Cylinders & Cartridges
- BCGA COP 44, The Storage of Gas Cylinders
- BCGA COP 36, Cryogenic Liquid Storage at Users’ Premises
- BCGA COP 19, Bulk LOx Storage at User’ Premises
- BOC Audit Checklist – Third Party Owned Vessels;-Task List GERTL002
- JSP 309
- JSP 317
- JSP 319
- JSP 375
- JSP 418
- JSP 426
- Defence Logistics Framework

Notes for completion

5.	Section 1 is mandatory and must be completed by all units. The remainder of the contents page lists types of installation which may be applicable to your Unit. After determining which sections are applicable, annotate the ‘Required’ column by deleting as applicable. For multiple installation sites, the unit are to produce additional copies of the relevant FGSAA section e.g a unit with 4 x BFIs would return one copy of Section 1 and four copies of Section 4; one for each installation.

6.	Units should establish and maintain a local hazard log to register findings of the assessment, in line with guidance provided in JSP 317 and JSP 319.

7.	In countries outside of the UK, JSPs 309, 317 & 319 standards will apply unless the host nation regulations are more stringent. This does not apply to Germany where local standards agreed in the SOFA are to be adhered to.

8.	Footnotes provide guidance for completion throughout the assessment.

9.	Serials in red or blue font identify High Hazards or Key Performance Indicators (KPIs), which will be logged by FGSR on a TLB specific Hazlog.

10.	Please use the last page of this document to provide any feedback on the assessment; positive or negative. User information is a vital tool which will be used by the FGSR to continually develop and improve the assessment process.
CONTENTS

Section	Pages	Required	Copies
Section 1: Publications, Risk Assessments, USRP, DSEAR and Trained Personnel. / Required for all FGSAA returns.	5-9	Yes	1
Section 2: Workshops & Servicing Bays. / For internal TLB use only (as required). Not required by for Self-Assessment or FGSR Regulatory Inspection.	10-13	Yes/No*
Section 3: Packed Fuel & Lubricant Storage Facilities. / Required completion for all Self-Assessments or FGSR Regulatory Inspections (if present).	14-18	Yes/No*
Section 4: Packed Waste Storage Facilities. / Required completion for all Self-Assessments or FGSR Regulatory Inspections (if present).	19-21	Yes/No*
Section 5: Mechanical Transport Fuelling Installations (MTFIs). / Required completion for all Self-Assessments or FGSR Regulatory Inspections (if present).	22-32	Yes/No*
Section 6: Oil Fuel Depot (OFD) & Petroleum Storage Depot (PSD). / Required completion for all Self-Assessments or FGSR Regulatory Inspections (if present).	33-43	Yes/No*
Section 7: Aviation Bulk Fuel Installations (BFIs). / Required completion for all Self-Assessments or FGSR Regulatory Inspections (if present).	44-61	Yes/No*
Section 8: JOFS. / Required completion for all Self-Assessments or FGSR Regulatory Inspections (if present).	62-66	Yes/No*
Section 9: Bulk Fuel Carrying Vehicle Storage Park. / Required completion for all Self-Assessments or FGSR Regulatory Inspections (if present).	67-72	Yes/No*
Section 10: Uninstalled Engine Test Facility (UETF). / Required completion for all Self-Assessments or FGSR Regulatory Inspections (if present).	73-78	Yes/No*
Section 11: Bulk Waste Installation. / Required completion for all Self-Assessments or FGSR Regulatory Inspections (if present).	79-82	Yes/No*
Section 12: Oil Pump Room & PRE. / Required completion for all Self-Assessments or FGSR Regulatory Inspections (if present).	83-84	Yes/No*
Section 13: Gas Cylinder Storage Facilities. / Required completion for all Self-Assessments or FGSR Regulatory Inspections (if present).	85-90	Yes/No*
Section 14: Cryogenic Liquid Storage Facilities. / Not required as part of a Self-Assessment. Annual FGSR Regulatory Inspection only.	91-97	Yes/No*
Section 15: Bulk LPG Storage Facilities. / Not required as part of a Self-Assessment. FGSR Regulatory Inspection only.	98-104	Yes/No*
Feedback Form / Complete as required.	105	Yes/No*

*Delete as applicable.
1.	Publications, Trained Personnel, DSEAR and Documentation

1.1 ACCESS TO AND FAMILIAR WITH FOLLOWING PUBLICATIONS[1]				GRADING
				G			R				N/A				Remarks

1.1.1	JSP 309
1.1.2	JSP 317
1.1.3	JSP 319
1.1.4	JSP 375
1.1.5	JSP 418
1.1.6	JSP 515
1.1.7	Defence Logistics Framework
1.1.8	DEF STAN 01-05 / Issue 17 dated Mar 11.
1.1.9	JSP 426

1.2 RISK/COSHH ASSESSMENTS				GRADING
				G			R				N/A				Remarks
Ref
1.2.1	JSP 375	All processes / activities involving Gases and Fuel & Lubricants (F&L) i.e. storage, handling, distribution, and maintenance of systems / plant, containing F&L, are potential hazardous activities which require accurate and in-date risk assessments to satisfy the requirements of JSP 375, which must be reviewed on an annual basis and signed by an appropriate person (i.e. Line Manager or H&S Rep).							FGSR Note: / Regulation – Condition of Certification / KPI
1.2.2	JSP 375	COSHH Risk Assessments have been carried out for all Gases and F&L products held within the unit, including waste. The assessments are readily available in all storage locations iaw the requirements of JSP 375.
1.2.3	JSP 375	Material Safety Data Sheets (MSDS) are readily available for all Gases and F&L products held within the unit, in all storage locations. These should be provided by the product manufacturer, but can also be downloaded from JSP 515, The Hazardous Stores Information System.
1.2.4	JSP 375	Has an Area Custodian been appointed (4Cs Duty Holder) wrt management of all fuel and gas compounds.
1.2.5	JSP 375	Site H&S RA / Has an Area Site Hazard Register been produced and is it maintained?
1.2.6	JSP 418	An Environmental Management System has been produced to manage all fuel related environmental risks identified in the Site RA.							FGSR Note: / Regulation – Condition of Certification / KPI

1.3 UNIT EMERGENCY RESPONSE PLANS				GRADING
				G				R				N/A				Remarks

Note: MoD Establishments based on coastlines, within MoD Dockyards, or in civilian harbours must ascertain if their F&L holdings pose any risk to the maritime environment. If so, the USRP, shall include both land & maritime spill response strategies & be formally included into the respective Queens Harbour Masters response plans accordingly.
All Sites
Ref
1.3.1	JSP 317 / JSP 319	Have suitable Fire Orders been produced for all fuel and gas installations at the site?
Bulk Fuel Storage Sites
1.3.2	JSP 317 Defence Intranet Page	Has the unit formulated a USRP which is fit for purpose?							FGSR Note: / Regulation – Condition of Certification / KPI
1.3.3	~ ~	Is there a Contents Page, with Annexes shown in bold to indicate their importance? Annexes should be flagged to enable swift access.
1.3.4	~ ~	Has the plan been amended within the last 12 months?
1.3.5	~ ~	Distribution List. The document has been distributed to each stakeholder.
1.3.6	~ ~	The Commanding Officers Foreword is present.
1.3.7	~ ~	The Commanding Officers Unit Safety and Environmental O&A Statement are present.
1.3.8	~ ~	A list of definitions is included in the plan to assist understanding.
1.3.9	~ ~	An Introduction to the document is included.
1.3.10	~ ~	A Mission Statement, which highlights the importance of protecting the environment and life, is included.
1.3.11	~ ~	An Action Plan which outlines the USRP processes is included.
1.3.12	~ ~	An outline of the unit Risk Assessment must be provided to indicate the potential risks that the USRP has been formulated to cover.
1.3.13	~ ~	Command & Control. An outline of the actions to be taken by those named within the USRP must be included.
1.3.14	~ ~	Service Support. An outline of the unit’s own support organisations, equipment and services must be provided.
1.3.15	~ ~	Outside Agencies. An outline of the external agencies that may be contacted in support of a spillage incident must be included. This should include Local Authorities, Emergency Services, Environmental Agencies and the Emergency Spillage Response Contractor.
1.3.16	~ ~	Command & Signal. An outline of the reporting actions required must be included.
1.3.17	~ ~	Communications. The type of communications to be used during initial, mobilisation & on-going operations must be detailed.
1.3.18	~ ~	Media. An outline of the actions to be taken in the event of media interest must be detailed and details of the Media Officer should be provided.
1.3.19	~ ~	Security. An outline of security measures to be taken in the event of a spillage to cordon and control the area around the spillage should be included.
1.3.20	~ ~	Health & Safety. An outline of unit general and specific H&S considerations should be included.
1.3.21	~ ~	Disposal of Contaminates. An outline of the process for the correct disposal of products, including waste, recovered after a spillage must be included.
1.3.22	~ ~	Training. An outline of training requirements for personnel named in the plan must be detailed.
1.3.23	~ ~	Exercise/practice. The plan must be practiced on an annual basis. The scale of the exercise must be appropriate for the site and based on adequate risk assessment – i.e. high risk sites holding large quantities of fuel may require a Major Exercise, whilst low risk sites holding small quantities of fuel may require an In-Unit Exercise. / Indicate in the remarks column when the USRP was last practised, the scale of the exercise, and if it was the appropriate scale.							FGSR Note: / Regulation – Condition of Certification / Last exercise:__________________ / Scale of ex:________ / Appropriate scale: Y/N
1.3.24	~ ~	Plan Review/Amendment. The plan must be reviewed annually and amended accordingly after an incident or exercise.
1.3.25	~ ~	Records. The plan should include a log of all key decisions and communications made with outside agencies during an incident.
1.3.26	~ ~	Reporting. To enable the appropriate level of support from TLBs & LAND SYSTEMS it is important that each incident is reported using SPILLREP & POLREP Parts 1 & 2.
1.3.27	~ ~	The following Annex and Appendices should be included in the plan: / Annex A – Action to be taken by a person discovering a spillage. / App 1 – Fuel Spillage Immediate Action Poster. / App 2 – Pollution Control Orders for BFCV Operators. / App 3 – Spillage action during deployed Ops/Exercise.
1.3.28	~ ~	The following Annex and Appendices should be included in the plan: / Annex B – Unit Actions/Duties on spillage incident. / App 1 – Duties of Guard/Ops Room. / App 2 – Duties of Incident Commander. / App 3 – Duties of Pollution Control Officer (PCO) / App 4 – Duties of Pollution Control Team (If Applicable) / App 5 – Duties of Maintenance Management Organisation (MMO) / App 6 – Duties of Media Officer / App 7 – Best Practice Guidance – Based on lessons learnt. / App 8 – MoD F7771 Establishment/Unit/Section Spillage Register. / App 9 – General Health & Safety Precautions.							Note: App 7 will only be required if the unit have had a previous spill.
1.3.29	~ ~	The following Annex and Appendices should be included in the plan: / Annex C - Contact Numbers. / App1 – Unit and Local Authority Numbers. / App 2 – MoD Emergency Pollution Response Contractors details.
1.3.30	~ ~	The following Annex and Appendices should be included in the plan: / Annex D – Spillage Reporting / App 1 – SPILLREP Part 1 – MoD F7772 / App 2 – SPILLREP Part 2 - MoD F7773 / App 3 – POLREP/SITREP – MoD F7774
1.3.31	~ ~	The following Annex and Appendices should be included in the plan: / Annex E - Pollution Response Equipment. / App 1 – Unit Pollution Control Sorbent (PCS) holdings. / App 2 – Pollution Control Equipment (PCE) available.
1.3.32	~ ~	The following Annex and Appendices should be included in the plan: / Annex F - Unit Plans. / App 1 – Site Plan – Location of PCP and First Aid response packs. / App 2 – Unit Drainage Plan (must include capacity and location of interceptor) / App 3 – Spillage Hazardous Zone Plan
1.3.33	~ ~	The following Annex should be included in the plan: / Annex G - Register of Hazardous Areas and Hazardous Products Held.
Bulk Gas Storage Sites – not required for self-assessment
1.3.34	JSP 319	Is there an Emergency Plan of the gas compound? / Emergency Procedures. Does the compound have comprehensive written Emergency Procedures and are they displayed? / Spills / Leaks / Fire / Action in the event of an emergency at a nearby facility / Question installation operator on actions to be taken.
1.3.35	JSP 319	Has the emergency plan been disseminated to emergency services & key stakeholders? (guardroom, SHEF Manager, Fire Officer)
1.3.36	JSP 319	Has a practical exercise of the emergency plan been conducted in the last 12 months? Is this recorded?
1.3.37	JSP 319	Are accidents, incidents and dangerous occurrences associated with gasses and their containers reported? Is a log kept? / Cryo – MF 7777, RIDDOR
All Sites
1.4 DSEAR 2002 [2]				GRADING
				G			R					N/A				Remarks
Ref
1.4.1	JSP 309	Those operating Defence fuel and industrial gas facilities must complete a suitable and sufficient Risk Assessment that complies with the Dangerous Substances and Explosive Atmosphere Regulations							FGSR Note: / Regulation – Condition of Certification / KPI
1.4.2	JSP 309	If an explosive atmosphere could exist then those operating Defence fuel and industrial gas facilities must implement a plan that identifies the Hazardous Areas. / Have Hazardous Area Classification Diagrams been completed?							FGSR Note: / Regulation – Condition of Certification / KPI
1.4.3	JSP 309	Those operating Defence fuel and industrial gas facilities must demonstrate that all electrical and mechanical machinery and portable equipment used in Hazardous Areas is identified as fit for purpose for the respective zones, is correctly maintained and is asset tracked in accordance with DSEAR.							FGSR Note: / Regulation – Condition of Certification / KPI

1.5 TRAINED PERSONNEL					GRADING
					G				R				N/A				Remarks
Bulk Fuel Storage Sites
Ref
1.5.1	JSP 317		Operating Authority Delegation. The role of Operating Authority (OA) ultimately rests with the Head of Establishment (HoE) who is required to exercise duty of care over all activities. However, the HoE may choose to formally delegate authority to an appropriate person, although overall responsibility must be retained. When authority is to be delegated, an OA is to be formally appointed by the HoE via a Letter of Appointment (LoA). / This is a mandatory requirement for personnel employed in the management and operation of aviation fuel installations. It is also recommended for ground fuel installations. / If the HoE has delegated OA, has an appropriate person been formally appointed via a LoA?
1.5.2	JSP 317		Units require an All Arms F&L Manager (F&L Supervisor), who has attended a formal course at either the Defence Petroleum Training Squadron (ground fuels) or RAF Halton (aviation fuels). The F&L Manager will be the units’ focal point for all F&L related matters and will be responsible for conducting formal and informal in-unit training for individuals who are employed within specific petroleum duties.						FGSR Note: / Regulation – Condition of Certification / KPI
1.5.3	JSP 317		Fuel installations may only be operated by personnel who are trained and competent to do so. A Certificate of Competence (COC) for each operator, specifying each installation the individual is authorised to operate, is to be held by the unit. Part G of the COC must be completed by the Operating Authority (OA), be they the HoE or a person who has had OA responsibilities formally delegated to them. / RAF personnel that are employed in F&L duties are to attend the RAF Halton F&L Operations Course as a pre-employment requirement. / **Note that COCs for Aviation BFIs and Ground Fuel MTFIs are now distinctly different. The unit must use the appropriate COC for the installation.						FGSR Note: / Regulation – Condition of Certification / KPI
1.5.4	FGSR SC		The units dedicated Authorising Engineer is ___________________. / This question should be graded as ‘Red’ if unknown.
1.5.5	FGSR SC		The units dedicated Authorised Person Petroleum is _______________. / This question should be graded as ‘Red’ if unknown.
Bulk Gas Storage Sites – not required for self-assessment
1.5.6	JSP 319		Are personnel who operate the gas infrastructure suitably qualified? / Cryogenic installations – CSG Stafford STC 1243 / General Bulk Gas Storage - Compressed Gases CN3252 / Note – External training is accepted, subject to TLB authority (onus on TLB to approve alternative trg courses).						FGSR Note: / Regulation – Condition of Certification / KPI
1.5.7	JSP 319		Is access to gas compounds restricted? Are personnel who enter the compounds competent to do so? Are non-operators briefed on safety precautions? Are records kept?
[1] Access to publications via the Defence Intranet is acceptable.
[2] Under normal storage conditions, full compliance with DSEAR is usually only applicable to Class I and II installations. An initial Risk assessment must be carried out for Class III installations, however hazardous area classification drawings will not normally be required, unless the fuel is being stored at or above its flammable temperature or at high pressure to give off a mist or spray. In this instance the fuel should be re-classified to Class II and full DSEAR compliance and hazardous area classification will be required.

2.	WORKSHOP AND SERVICING BAYS

APPLICABLE TO SECTION 2
OPERATION & FUNCTION					Information only
Note: In countries outside of the UK JSP 317 standards will apply unless the host nation regulations are more stringent. This does not apply to Germany where local standards in compliance with SOFA are to be adhered to.
WORKSHOPS
2.1 FIRE, HEALTH & SAFETY					GRADING
					G	R	N/A	Remarks
Ref
2.1.1	JSP 317			Combat of F&L Health Hazards. Washing & changing facilities provided at the place of work. Barrier and After Work Cream provided. Provision of Eyewash & First Aid.
2.1.2	JSP 317			Appropriate PPE is provided for all employees and is worn at all times when undertaking petroleum duties.
2.1.3	JSP 317			An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan
2.1.4	JSP 317			The extent of the hazardous area is to be clearly indicated with the use of notices stating “Petroleum Spirit. Highly Flammable- No Smoking –No Naked Lights” (Overseas dual language signs), as follows:
2.1.5	JSP 317			Fire Safety Notices & Fire Action Notices must be displayed in order to comply with the Health and Safety (Safety Signs and Signals) Regulations 1996. Locations and quantities should relate to the local risks and be the result of a risk assessment.
2.1.6	JSP 317			Smoking or Smoking materials are not permitted in the hazardous area. Personnel are to deposit any smoking materials in a safe designated contraband area before entering a hazardous zone or likely hazardous area.
2.1.7	JSP 317			Where drums or other large containers are required to be moved by hand, cradles or trolleys are to be provided to minimise product spillage and injury to personnel.
2.1.8	JSP 317			Storage Cabinets must be Fire Resistant and designed to BS 476 specification. (NSN F3 7125-99-700-4418).
2.1.9	JSP 317			The cabinet should be sited in a designated area, at least 3m from working area but preferably 5m and not below any openings or exits.
2.1.10	JSP 317			The following HWS must be displayed on all F&L cabinets:

2.2 ENVIRONMENTAL PROTECTION					GRADING
					G	R	N/A	Remarks
Ref
2.2.1	JSP 317	Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
2.2.2	JSP 317	Spillage Immediate Action Posters are to be prominently displayed at all Pollution Control Points and locations were F&L is stored.

2.3 OPERATING PROCEDURES					GRADING
					G	R	N/A	Remarks
Ref
2.3.1	JSP 317		Container Markings. The correct product information is to be marked on each container. Markings are to be legible.
2.3.2	JSP 317		Oxidisers or Acids. Are not to be stored with flammable liquids.
2.3.3	JSP 317		Housekeeping. No general rubbish, all contaminates removed from the area including rags after use.
2.3.4	JSP 317		Large Drums. Containers with a capacity of no greater than 200 Ltrs and intended for use on the same day or shift may be stored temporarily outside a building providing the container is properly closed and labelled and the building wall is a fire wall.
2.3.5	JSP 317		Unused Containers. To be returned to the storage area at the end of the working day or shift.
2.3.6	JSP 317		Empty Containers. All empty container closures to be closed.
2.3.7	JSP 317		Working Stock. Up to 50 Ltrs of class 3.1 or 3.2 & 250 Ltrs of Class 3.3 Unclassified, can be stored in the workplace providing serials 2.1.1.8 – 2.1.1.10 are complied with.
2.3.8	JSP 317		Each locker is to display an up to date contents list which is to be annotated with the batch number and re-test dates of all products held.
2.3.9	JSP 317		Life expired products which are unidentifiable due to degradation of labels are to be quarantined and segregated from ‘In use’ stock pending disposal or investigation.
2.3.10	JSP 317		User Units. Officers in charge are responsible for ensuring the quality and integrity of all F&L products held in their unit.
SERVICING BAY
2.4 FIRE, HEALTH & SAFETY					GRADING
					G	R	N/A	Remarks
Ref
2.4.1	JSP 317			Combat of F&L Health Hazards. Washing & changing facilities provided at the place of work. Barrier and After Work Cream provided. Provision of Eyewash & First Aid.
2.4.2	JSP 317			Appropriate PPE is provided for all operators.
2.4.3	JSP 317			The extent of the hazardous area is to be clearly indicated with the use of notices stating “Petroleum Spirit. Highly Flammable- No Smoking –No Naked Lights” (Overseas dual language signs), as follows:
2.4.4	JSP 317			Fire Safety Notices & Fire Action Notices must be displayed in order to comply with the Health and Safety (Safety Signs and Signals) Regulations 1996. Locations and quantities should relate to the local risks and be the result of a risk assessment.
2.4.5	JSP 317			Smoking or Smoking materials are not permitted in the hazardous area. Personnel are to deposit any smoking materials in a safe designated contraband area before entering a hazardous zone or likely hazardous area.
2.4.6	JSP 317			Where drums or other large containers are required to be moved by hand, cradles or trolleys are to be provided to minimise product spillage and injury to personnel.
2.4.7	JSP 317			Storage Cabinet. Fire resistant. BS 476. (NSN F3 7125-99-700-4418).
2.4.8	JSP 317			The cabinet should be sited in a designated area, at least 3m from working area but preferably 5m and not below any openings or exits.
2.4.9	JSP 317			The following HWS must be displayed on all F&L cabinets:

2.5 ENVIRONMENTAL PROTECTION					GRADING
					G	R	N/A	Remarks
Ref
2.5.1	JSP 317			Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
2.5.2	JSP 317			Spillage Immediate Action Posters are to be prominently displayed at all Pollution Control Points and locations were F&L is stored.

2.6 OPERATING PROCEDURES					GRADING
					G	R	N/A	Remarks
Ref
2.6.1	JSP 317			Container Markings. The correct product information is to be marked on each container. Markings are to be legible.
2.6.2	JSP 317			Oxidisers or Acids. Are not to be stored with flammable liquids.
2.6.3	JSP 317			Housekeeping. A good housekeeping standard is to be maintained. Rubbish and refuse of any kind is to be removed.
2.6.4	JSP 317			Large Drums. Containers with a capacity of no greater than 200 Ltrs and intended for use on the same day or shift may be stored temporarily outside a building providing the container is properly closed and labelled and the building wall is a fire wall.
2.6.5	JSP 317			Unused Containers. To be returned to the storage area at the end of the working day or shift.
2.6.6	JSP 317			Empty Containers. All empty container closures to be closed.
2.6.7	JSP 317			Working Stock. Up to 50 Ltrs of class 3.1 or 3.2 & 250 Ltrs of Class 3.3 Unclassified, can be stored in the workplace providing serials 2.2.1.8 – 2.1.1.10 are complied with.
2.6.8	JSP 317			Each locker is to display an up to date contents list which is to be annotated with the batch number and re-test dates of all products held.
2.6.9	JSP 317			Life expired products which are unidentifiable due to degradation of labels are to be quarantined and segregated from ‘In use’ stock pending disposal or investigation.
2.6.10	JSP 317			User Units. Officers in charge are responsible for ensuring the quality and integrity of all F&L products held in their unit.

2.7 BULK FUEL CARRYING VEHICLE SERVICING BAY / Note: These additional questions are only applicable to units with purpose built BFCV Servicing Bays.					GRADING
					G	R	N/A	Remarks
Ref
2.7.1	D&MG 13, Para 3.4			Internal Walls. Are to be provided with imperforate 1 hour rated fire walls, with no internal access doors.
2.7.2	As above			Ventilation. If supplied from a common plant room all ductwork should be provided with fire dampers at the point of duct penetration to the bay
2.7.3	As above			Earthing Points. Recessed earthing points (with a resistance of 10 ohms or less) each side of the bay every 5m.
2.7.4	As above			Electrical Equipment. Zone 1 in accordance with BS 5345 throughout the entire servicing bay.				FGSR Note: / Regulation
2.7.5	JSP 317			Lightning Protection. To be installed in compliance with BS 6651 or BS EN 62305*.				*Installations installed on or after 31 Aug 08.
2.7.6	JSP 317			Hazard Warning Signs(HWS). The following HWS must be displayed on all approaches to the facility:

3.	PACKED FUEL AND LUBRICANT STORAGE FACILITIES

3.1 OPERATION & FUNCTION				GRADING
				G		R		N/A		Remarks
Ref
3.1.1	JSP 317		Security. Installations should be protected by security fences unless inherently secure, as within a secure area.
3.1.2	JSP 317		Minimum Separation Distances. Packed stocks in open-air compounds need to have sufficient separation distances from potential sources of ignition, boundaries, public roads, railway lines and occupied buildings. The following distances, determined by quantity of F&L products stored, should be imposed: / Quantity Stored (Ltrs) Minimum Separation Distance (m) / < 1000 2 / 1001- 100,000 4 / > 100,000 7.5 / In addition the maximum stack size should not exceed 300,000 Ltrs. If this quantity is stored the minimum separation distance between stacks is to be 4 m.
3.1.3	JSP 317		Fire Walls. If employed no separation distance between products is required. Wall must be as high as container stack, be a min of 2m high and located within 3m of stack. Provided these conditions are met, the fire wall may form part of the bund wall, building wall or boundary wall.
3.1.4	JSP 317		Re-Packing Room. A separate room is required for repackaging of damaged containers, which can also act as a quarantine and transit area. This room does not have to be part of the storage facility, however in an open compound a segregated area with drip trays must be provided.
3.1.5	JSP 317		Acid. If stored physical segregation, or preferably, a dedicated storage room is required. In addition, an Eyewash Station and Emergency Drench Shower must also be provided in an area adjacent to the store.
3.1.6	JSP 317		Containment within buildings. If stored inside a 75 mm retention sill should surround the store. If this can’t be achieved, the floor should be recessed to this depth, sloping towards a sump with sufficient capacity to contain 110% of the largest container stored. An alternative, acceptable method could be achieved with the provision of 150 mm retaining sill, which surrounds the entire facility. In this instance a sump would not be required.
3.1.7	JSP 317		Aqueous Products. If aqueous dangerous goods e.g AL 39 or marine pollutants are stored, the area must be bunded or so arranged to prevent any spillage from entering the drainage system.
3.1.8	JSP 317		Bunds. Bunds of open air compounds are to be of sufficient capacity to contain 110% of the largest container stored. A means of removing accumulated water from the bund is required and the contaminated water must be disposed of as hazardous waste.
3.1.9	JSP 317		Access Ramp. Access ramps to either closed or open-air storage facilities are to have a maximum slope of 1 in 15.
3.1.10	JSP 317		Fire Protection. F&L Stores and Buildings should be constructed using non-combustible materials. They should be fitted with a Lightweight roof to act as an explosive relief conduit or alternatively have relief panels fitted to one or more exterior walls, provided they vent to a safe place.
3.1.11	JSP 317		Means of Escape. The distance of travel to a means of escape is not to exceed more than 9 m in one direction. If a means of escape is provided in more than one direction the maximum travel distance between exits is limited to 18 m. Emergency exits should be obvious and gangways are to be a minimum of 1.5 m in width. Exits are to open outwards and are to be immediately operable using a single action device which doesn’t require a key.
3.1.12	JSP 317		Electrical Equipment. The electrical equipment designated is to be Zone 2, Ex N. The most onerous temperature class is to be determined by the product range to be stored. BS EN 60079-01-2006 refers.						FGSR Note: / Regulation
3.1.13	JSP 317		Lighting. Is to be installed to provide an average luminance of 200 Lux at 0.8m above ground level.
3.1.14	JSP 317		Lightning Protection. A lightning protection system compliant with BS 6651 or BS EN 62305* is to be installed.						*Installations installed on or after 31 Aug 08.
3.1.15	JSP 317		Ventilation. Ventilation openings are to have a total area equivalent to 1-3% of the total external wall area. For small buildings the simplest method of ensuring adequate ventilation is to have fixed, permanent openings, such as air bricks or louvers installed in the external walls at high and low levels.
3.1.16	JSP 317		Hazard Warning Signs(HWS). The following HWS stating “Petroleum Spirit, Highly Flammable, No Smoking, No Naked Lights” must be displayed on all approaches to the facility:

3.2 FIRE, HEALTH & SAFETY				GRADING
				G		R		N/A		Remarks
Ref
3.2.1	MoD(A) FF&FS Sec 3 Ch 2 P 5		Other Stores. Facility to be used exclusively for the storage of F&L.
3.2.2	MoD(A)FF&FS Sec 3, Ch 2, P 35 d		Glazing. All windows within the building, if applicable, are to be fitted with fire resistant glazing. (Highly Flammable products only – Flashpoint of 32ºc or below).
3.2.3	JSP 317		Washing & changing facilities are to be provided for personnel at the place of work. In addition, the following items must also be provided: / Barrier Cream and After Work Cream. / Eyewash (In Date). / Emergency First Aid Kit.
3.2.4	JSP 317		Appropriate Personal Protective Equipment (PPE) and Respiratory Protective Equipment (RPE) is provided and used by all operators.
3.2.5	JSP 317		The quantity and location of all fire fighting equipment, which is determined by the Unit Fire Officer, must reflect what is stated in the Fire Safety Risk Assessment (FSRA).

3.2.6	JSP 317		An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan
3.2.7	JSP 317		Fire Safety Notices & Fire Action Notices must be displayed in order to comply with the Health and Safety (Safety Signs and Signals) Regulations 1996. Locations and quantities should relate to the local risks and be the result of a risk assessment.
3.2.8	JSP 317		Smoking or Smoking materials are not permitted in the hazardous area. Personnel are to deposit any smoking materials in a safe designated contraband area before entering a hazardous zone or likely hazardous area.
3.2.9	JSP 317		Grass and Vegetation is to be cut back to a minimum of 15m. Isolated deciduous trees are permitted but conifers must be removed. Grass cutting and removal of vegetation must be carried out iaw the MoD Safety Rules and Procedures for Work on Petroleum installations.
3.2.10	JSP 317		The installation should have an effective means of both raising the alarm and giving warning in case of fire. It should be audible to all those likely to be effected by the fire. There must be access to a phone with in reasonable distance, which is to be clearly signposted.

3.3 ENVIRONMENTAL PROTECTION				GRADING
				G		R		N/A		Remarks
Ref
3.3.1	JSP 317		Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
3.3.2	JSP 317		Leaking Containers. The storage area should be inspected regularly for evidence of leaking containers. If found, leakers should be decanted into sound containers specifically designed for the storage of F&L.
3.3.3	JSP 317		A Pollution Control Point (PCP) is to be established at the installation. The PCP must be clearly identifiable, stocked appropriately and be maintained on a regular basis.
3.3.4	JSP 317		Spillage Immediate Action Posters are to be prominently displayed at all Pollution Control Points and locations were F&L is stored.

3.4 OPERATING PROCEDURES				GRADING
				G		R		N/A		Remarks
Ref
3.4.1	JSP 317	Container Markings. The correct product information is to be marked on each container. Markings are to be legible.
3.4.2	JSP 317	Housekeeping. No general rubbish and all contaminates, including rags, are to be removed from the area after use.
3.4.3	JSP 317	Only authorised equipment, plant, vehicles or locomotives may enter the hazardous area.
3.4.4	JSP 317	Gas bottles, including medical gases, whether full or empty are to be stored separately from packed F&L stock.
3.4.5	JSP 317	Leak Detection. Containers are to be stacked in such a manner that leaks can be easily detected.
3.4.6	JSP 317	25 Ltr Drums (Indoors). Preferably stored in F&L Schaefer Pallets. If no pallets available drums should be stacked upright with each tier inset half a drum. Where the design of the drum makes this method impractical they may be stored directly on top of each other to a maximum of 5 tiers high.
3.4.7	JSP 317	25 Ltr Drums (Outdoors). Preferably stored in F&L Schaefer Pallets. If unavailable belly stack drums in rows of 2, butt to butt, up to a maximum of 5 tiers high. Filler caps to face outward and be just below the level of the liquid. A 2 m wide lane is to be left between each double row.
3.4.8	JSP 317	205 Ltrs Drums. Belly stacked as above in rows of 2. Usually 1 tier high, however if real estate is restricted this can be extended to 3 tiers. Drums must be stored on hard, dry standings.
3.4.9	JSP 317	Jerricans. Preferably stored in F&L Schaefer Pallets up to 4 tiers high if real estate permits. If stored on uneven ground jerricans are to be belly stacked up to a maximum of 10 tiers high.
3.4.10	JSP 317	Greases. Grease in individual tins or kegs should be stacked upright not more than 5 Tiers high and be inset by half a tin diameter at each tier. Wherever possible, grease should be stored under cover.
3.4.11	JSP 317	Cartons. Preferably stored in F&L Schaefer Pallets. Stacked under cover where possible up to 6 tiers high. If no pallets available kept off the ground using metal or brick dunnage.
3.4.12	JSP 317	Palletised Containers. . Palletised Stack height is limited to the MHE available. Larger lanes should be left to allow MHE to manoeuvre, however the minimum recommended safety distances must never be reduced.
3.4.13	JSP 317	Empty Containers. Closures closed, bungs replaced and screwed tight.
3.4.14	JSP 317	Cradles or Trolleys. To be provided when movement of large drums is to be undertaken by hand.
3.4.15	JSP 317	Segregation. Packed F&L should be segregated by product type, UN Classification, Batch Number, Fill and Re-test dates and each location is to be labelled accordingly
3.4.16	JSP 317	Fit For Issue. The quality and integrity of the packed F&L is to be maintained at all times. All stock held should be fit for purpose and should have sufficient life left to allow for consumption by the user before a retest is due. Product that is life expired is identified and segregated from other stock.
3.4.17	JSP 317	Unit Filled Cans. In exceptional circumstances Unit Commanders may authorise an Officer or NCO to fill jerricans from an MTFI. In this instance all previous labels must be removed from the cans prior to filling and a Unit Filled Identification Label must be fitted. Unit Filled cans are to be used within 3 months of fill date.

3.5 MAINTENANCE					GRADING
					G		R		N/A		Remarks
Ref
3.5.1	DIO / PG 06/12	The Packed F&L Storage Facility (Indoor) has been inspected and deemed compliant by a competent member of the Maintenance Management Organisation in accordance with the requirements of the DIO Practitioners Guide 06/12.

4.	PACKED WASTE STORAGE FACILITIES

An uncontrolled release of waste F&L would have the same impact on the environment as serviceable F&L. Therefore packed waste storage shall comply with principles laid down at JSP 317.
4.1 OPERATION & FUNCTION				GRADING
				G	R	N/A	Remarks
Ref
4.1.1	JSP 317	Security. Installations should be protected by security fences unless inherently secure, as within a secure area.
4.1.2	JSP 317	Minimum Separation Distances. Packed stocks in open-air compounds need to have sufficient separation distances from potential sources of ignition, boundaries, public roads, railway lines and occupied buildings. The following distances, determined by quantity of F&L products stored, should be imposed: / Quantity Stored (Ltrs) Minimum Separation Distance (m) / < 1000 2 / 1001- 100,000 4 / > 100,000 7.5 / In addition the maximum stack size should not exceed 300,000 Ltrs. If this quantity is stored the minimum separation distance between stacks is to be 4 m.
4.1.3	JSP 317	Aqueous Products. If aqueous dangerous goods e.g AL 39 or marine pollutants are stored, the area must be bunded or so arranged to prevent any spillage from entering the drainage system.
4.1.4	JSP 317	Bunds. Bunds of open air compounds are to be of sufficient capacity to contain 110% of the largest container stored. A means of removing accumulated water from the bund is required and the contaminated water must be disposed of as hazardous waste.
4.1.5	JSP 317	Access Ramp. Access ramps to either closed or open-air storage facilities are to have a maximum slope of 1 in 15.
4.1.6	JSP 317	The following Hazard Warning Sign stating “Petroleum Mixture, Highly Flammable, No Smoking or Naked Flames, No Mobile Phones, No Parking” must be displayed on all approaches to the facility:

4.2 FIRE, HEALTH & SAFETY				GRADING
				G	R	N/A	Remarks
Ref
4.2.1	MoD(A) FF&FS Sec 3 Ch 2 Para 5	Other Stores. Facility to be used exclusively for F&L.

4.2.2	JSP 317	Washing & changing facilities are to be provided for personnel at the place of work. In addition, the following items must also be provided: / Barrier Cream and After Work Cream. / Eyewash (In Date). / Emergency First Aid Kit.
4.2.3	JSP 317	Appropriate Personal Protective Equipment (PPE) and Respiratory Protective Equipment (RPE) is provided and used by all operators.
4.2.4	JSP 317	The quantity and location of all fire fighting equipment, which is determined by the Unit Fire Officer, must reflect what is stated in the Fire Safety Risk Assessment (FSRA).
4.2.5	JSP 317	An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan
4.2.6	JSP 317	Fire Safety Notices & Fire Action Notices must be displayed in order to comply with the Health and Safety (Safety Signs and Signals) Regulations 1996. Locations and quantities should relate to the local risks and be the result of a risk assessment.
4.2.7	JSP 317	Smoking or Smoking materials are not permitted in the hazardous area. Personnel are to deposit any smoking materials in a safe designated contraband area before entering a hazardous zone or likely hazardous area.
4.2.8	JSP 317	Grass and Vegetation is to be cut back to a minimum of 15m. Isolated deciduous trees are permitted but conifers must be removed. Grass cutting and removal of vegetation must be carried out iaw the MoD Safety Rules and Procedures for Work on Petroleum installations.
4.2.9	JSP 317	Housekeeping. No general rubbish and all contaminates, including rags, are to be removed from the area after use.
4.2.10	JSP 317	Only authorised equipment, plant, vehicles or locomotives may enter the hazardous area.
4.2.11	JSP 317	Gas bottles, including medical gases, whether full or empty are to be stored separately from packed waste F&L.
4.2.12	JSP 317	The installation should have an effective means of both raising the alarm and giving warning in case of fire. It should be audible to all those likely to be effected by the fire. There must be access to a phone with in reasonable distance, which is to be clearly signposted.

4.3 ENVIRONMENTAL PROTECTION			GRADING
			G		R	N/A	Remarks
Ref
4.3.1	JSP 317	Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
4.3.2	JSP 317	A Pollution Control Point (PCP) is to be established at the installation. The PCP must be clearly identifiable, stocked appropriately and be maintained on a regular basis.
4.3.3	Example USRP	Spillage Immediate Action Posters are to be prominently displayed at all Pollution Control Points and locations were F&L is stored.

4.4 OPERATING PROCEDURES				GRADING
				G	R	N/A	Remarks
Ref
4.4.1	JSP 317	Segregation. Different types of waste are to be stored separately to avoid the risk of fire, explosion or toxic vapour. Waste products should be collected and mixed into one of the following groupings as detailed in JSP 317, Part 3, Chapter 4, Annex A: / Mineral Oils / Fuel / Glycol’s, Glycol Ethers (AL’s) / Waste drums should be labelled with the specific group heading, prefixed by the word ‘Waste’ and followed by the word ‘Only’, e.g:
4.4.2	JSP 317	Leak Detection. Containers are to be stacked in such a manner that leaks can be easily detected.
4.4.3	JSP 317	Leaking Containers. The storage area should be inspected regularly for evidence of leaking containers. If found, leakers should be decanted into sound containers specifically designed for the storage of F&L.
4.4.4	JSP 317	Empty Containers. Closures to be closed, bungs replaced and screwed tight.
4.4.5	JSP 317	Cradles or Trolleys. To be provided when movement of large drums is to be undertaken by hand.

5.	MECHANICAL TRANSPORT FUELLING INSTALLATION (MTFI)

STORAGE TANKS
Tank / No.	Capacity	Product	Above/ / Below Ground	Construction / (GRP/Steel-Double/Single Skin)	Integrally Bunded	Redundant	Decommissioned	Remarks

METERING/DISPENSE PUMPS
Pump / No.	Serial No	Make	Product	Remarks

INTERCEPTORS
Int No.	Construction (GRP/Brick/Steel)	Max Capacity (Ltrs)	Type (Full Retention or Bypass)	Class (1 or 2)	Remarks

ANY ADDITIONAL INFORMAT ION
Annual ULGAS throughput Ltrs. / Unit ULGAS dependant Vehicles . / Does the throughput or number of dependant vehicles suggest that the unit could remove ULGAS from the site? Y/N

MTFI
5.1 INSTALLATION MAINTENANCE DOCUMENTATION					GRADING
					G		R				N/A			Remarks
Note: BF (G) based units will be inspected under an alternative regime. DSA FGSR should be contacted for guidance when completing this section
Ref
5.1.1			DIO Practitioner Guide / PG 06/12			Inspection of the Fuel Infrastructure and Flammable Goods Facilities (Previously known as Task 249) : / An Inspection of the Fuel Infrastructure and Flammable Goods Facilities was carried out on _____________. A Certificate of Fitness for Continued Use was Issued for a period of _____ months . If the facility was considered ‘Not Fit For Continued Use’ or the unit were given a specified timeframe to rectify observations in the ‘Table of Defects’, which has lapsed without rectification, grade this question as Red and answer the following ‘Action Plan’ question. / *If this question is graded Red, answer the following Action Plan question.					FGSR Note: / Regulation – Condition of Certification / KPI
5.1.2			As above.			Inspection of the Fuel Infrastructure and Flammable Goods Facilities Action Plan (If applicable): / An Action Plan has been produced and funding has been allocated to rectify the specific observations detailed in the ‘Table of defects’ which warranted the ‘Not Fit for Continued Use’ grading.					If green, send copy with completed report
5.1.3			D&MG 14 / Para 15.2 / Table 1 / APEA / Blue Book			Electrical Systems Test (Annual): / The Installations Electrical System was tested iaw the requirements of DMG 14 on ____________ by a Compex 7&8 qualified electrician or equivalent using the correct, serialised ‘Filling Station Electrical Periodic Inspection Report’ forms* and was graded as ‘Satisfactory’. An ‘Unsatisfactory’ grade should be awarded ‘Red’. / *If this question is graded Red, answer the following Electrical Test Action Plan question.					FGSR Note: / Regulation – Condition of Certification / KPI / *If the incorrect forms are used and the test is graded ‘Satisfactory’ award a green grade and provide required report template for next inspection.
5.1.4			As above.			Electrical Systems Test Action Plan (If applicable): / An Action Plan has been produced and funding has been allocated to rectify the specific observations which resulted in the ‘Unsatisfactory’ Electrical Test grading.					If green, send copy with completed report
5.1.5			JSP 317			Lightning Protection (If applicable) / If the installation is located in an area susceptible to lightning / BS 6651 and BS EN 62305 are to be consulted to determine whether lightning protection is required. If it is required, protection installed at installations constructed prior to 31 Aug 08 is to be maintained iaw the requirements of BS 6651 until such time that the installation is upgraded, after which BS EN 62305 will apply. Lightning protection installed on or after 31 Aug 08 is to be installed and maintained iaw the requirements of BS EN 62305.
5.1.6			D&MG 14 / Para 15.2 / Table 1			Metering Pump Calibration (6 Monthly): / The installation metering pumps were calibrated on ___________

5.1.7			DIO PG 06/12 / Annex B			Level 1 Assessment (Underground Single Skinned Steel Tanks (USSST) only): / Level 1 Assessments were conducted on __________ and the cumulative scores were_____________________.					A tank is deemed to be at high risk if the cumulative score exceeds the value of 6.
5.1.8			DE PG 06/12 / Annex B / D&MG 14 / Para 15.2 / Table 1			Level 2 Testing, Tank Tightness Tests for USSST only: / The Installations was constructed in________. The last Level 2 Testing was undertaken on the installations storage tanks on ________. The next Tank Tightness Tests are due on ___________					MTFI USSST shall undergo Level 2 testing in years 20, 25, 30 and every 2 years thereafter as a minimum and more frequently if the inspector deems it necessary.
5.1.9			JSP 317			Oil Water Interceptor (OWI) Design: / The OWI should meet the following specifications: / Minimum capacity of 7600 litres; and greater than the smallest compartment of the delivery tanker / Full retention / Class 1 (if draining to Surface or Foul Water) or Class 2 (if draining to Foul Water only) / If it does not meet the above conditions, and an Environmental Risk Assessment has not been produced to mitigate this risk, a ‘Red’ grade must be awarded for this question. / If an Environmental Risk Assessment has been produced; which mitigates the design shortcomings, this question can subsequently be graded as Green. / If the OWI does not meet the above specifications; answer the following mitigation question below.					FGSR Note: / KPI
5.1.10			JSP 317			OWI Mitigation - Pollution ERA: / A Pollution ERA, which has been updated within the previous 12 months, has been produced to mitigate the increased risk created by the inadequate OWI design. / If the Pollution ERA mitigates the inadequate OWI design by demonstrating a solution that is equivalent or better than the protection afforded by a suitable OWI, subsequent assessments can be assessed as Green.					FGSR Note: / NA in Germany where host nation standards take precedence.
5.1.11			JSP 317 / DMG 14 / Para 15.2 / Table 1			OWI Maintenance: These assets are maintained under Project Aquatrine by Aquatrine Service Providers. As a minimum, every 6 months or iaw manufacturers’ instructions, OWIs should be physically inspected to: / Ensure the Integrity of OWI / Identify the quantity of any accumulated F&L and silt. / Confirm that all electrical equipment is functioning correctly i.e Alarms. / Inspect the Condition of any coalescing devices and replace if necessary. / There must be evidence to clearly demonstrate that all the above points have been completed for this serial to be graded compliant. / The last inspection of the Interceptor was conducted by ___________ on ___________. If this date exceeds 6 months or the date of the last inspection cannot be ascertained award a ‘Red’ grade for this question.					FGSR Note: / In addition the Aquatrine contract only includes mainland UK units. In all other instances host nation standards will apply. / KPI

5.2 OPERATION & FUNCTION					GRADING
					G		R					N/A		Remarks
Ref
5.2.1			JSP 317	If the installation dispenses Petroleum (IP Class 1)and the following criteria is met, a Stage 1b vapour recovery system must be fitted: / Throughput is greater than 100,000 Ltrs per year. / The installation is in England or Wales / Installations in the Highlands and Islands of Scotland do not require vapour recovery.
5.2.2			JSP 317	An in-date Defence Safety Authority (DSA) ‘Certificate for Continued Operation’ must be displayed at the installation control point.					Delete as applicable: / Annual-FGSR to inspect / 3 Yearly / 5 Yearly
5.2.3			JSP 317	All Metering pumps/dispensers shall be marked with the NATO product and grade identification markings.
5.2.4			JSP 317	Does the installation layout provide adequate escape routes for personnel and means of access for fire brigades in the event of fire?
5.2.5			JSP 317	Overhead Power Cables must not cross the Petroleum Hazardous Area.
5.2.6			JSP 317	Above Ground Storage Tanks- Secondary Containment The bund wall must be capable of retaining 110% of the largest container within the bund or 25% of the aggregate of multiple containers, whichever is greater.
5.2.7			JSP 317	Above Ground Storage Tanks- Secondary Containment The bund wall must: / Be impervious to liquid / Not normally be higher than 1.5m high. / Be fitted with crash protection if susceptible to impact damage e.g adjacent to a vehicle manoeuvring area.
5.2.8			JSP 317	Above Ground Storage Tanks- Secondary Containment. In order to prevent jetting; a phenomenon caused when the primary container fails and F&L is propelled at force beyond the secondary containment, the bund wall is not to be constructed too close to the tank.
5.2.9			JSP 317	Above Ground Storage Tanks - Secondary Containment The bund base and walls must not be penetrated by any valve, pipe or other opening which is used for draining the bund. Where a tank fill or draw off pipe must pass through the bund base or wall, the hole must be carefully sealed with a fire resistant seal to prevent oil escaping.
5.2.10			JSP 317	Above Ground Storage Tanks - Secondary Containment Rainwater which collects in the sump must be removed on a regular basis to ensure the bund capacity is maintained. This water is to be disposed of appropriately to ensure no pollution occurs.
5.2.11			JSP 317	Inspection of Bunds - Bunds should be regularly inspected for signs of damage and checked for water by the operator on a weekly basis.
5.2.12			JSP 317	Above Ground Storage Tanks - Secondary Containment If oil or a mixture of oil and water is found in the bund it must be disposed of in accordance with current Hazardous Waste Regulations.
5.2.13			Oil Storage Regs 3 (3)	Above Ground Storage Tanks- Secondary Containment Valves should be as resistant to unauthorised interference and vandalism as far as is feasibly possible, with lockable or removable hand wheels.
5.2.14			OSR 01 / Reg 3(3)	Above Ground Storage Tank- Secondary Containment s All tank vent pipes, valves, filters, sight gauges and any other ancillary equipment with the exception of the fill pipe, draw off pipe or pump if the fuel has a flashpoint of less than 32ºc, must be positioned within the bund wall.
5.2.15			OSR 01 / Reg 3(3)	Above Ground Storage Tanks Valves should be marked to indicate whether they are open or closed, kept locked when not in use and fitted with a blanking cap or plug.
5.2.16			OSR 01 / Guidance Para 38	The connection point is to be located inside bund wall or be located in a position which allows for containment
5.2.17			JSP 317	Sight Glasses The use of sight glasses should be limited to the storage of Class II & III fuel tanks with a maximum capacity of 3500 Ltrs. If sight glasses are fitted they shall: / Be located in the secondary containment. / Be properly supported so that they cannot come loose. / Be fitted with a valve that automatically closes when the sight glass is not in use. / Be fitted with valves which are kept closed when not in use and only opened when taking contents readings.
5.2.18			JSP 317	Small Tank Minimum Separation Distances. A small tank is considered to be a tank with a diameter of less than 10m. The minimum separation distances from site boundaries, fixed sources of ignition, buildings and process areas for single small tanks are as follows: / Tank Capacity (m³) Separation (m) / Less than or equal to 1 1* / Greater than 1 and less than or equal to 5 4 / Greater than 5 and less than or equal to 33 6 / Greater than 33 and less than or equal to 100 8 / *In this instance the tank must be sited at least 2m from doors, plain glazed windows, other openings or means of escape. In addition they must not be below openings from an upper floor, regardless of vertical distance.
5.2.19			JSP 317	The installation must be protected by an independent Forecourt Separator/Oil Water Interceptor (OWI). Under no circumstances should waste water from washing, cleaning or fire fighting activities be discharged through a forecourt separator as the detergents will cause emulsification and render the device useless.					FGSR Note: Host nation standards take precedence in Germany.
5.2.20			JSP 317	The OWI must be fitted with a high-level alarm & automatic shut off valve.					FGSR Note: Host nation standards take precedence in Germany
5.2.21			JSP 317	The Road Tanker Delivery Stand should be located in a safe, well ventilated position in the open and should offer a clear, unobstructed forward escape route.					FGSR Note: / Regulation – Condition of Certification
5.2.22			JSP 317	The Road Tanker Delivery Stand – Attended. Prior to a bulk receipt at an attended installation, the delivery driver must be presented with a notice detailing safe delivery/receipt and emergency procedures. The driver is to read and sign the notice to confirm they understand the procedures before commencing delivery.
5.2.23			JSP 317	The minimum recommended distance of a Road Tanker Delivery Stand from occupied buildings, the site boundary or a fixed source of ignition is 10m or the distance calculated on the DSEAR RA; whichever is greater. This does not apply to Bulk Waste, UETF, FFO and Domestic Heating Tanks.					FGSR Note: / KPI
5.2.24			JSP 317	The Road Tanker Delivery Stand. The delivery stand should be a minimum of 15m x 5m. If this isn’t practicable, signage and barriers are to be used to restrict vehicle and personnel access during transfer operations.
5.2.25			JSP 317	The Road Tanker Delivery Stand. Road tankers shall not be made to wait on public or internal busy roads. The delivery stand should be substantially level to ensure full extraction during deliveries. If the delivery stand is in close proximity to an above ground storage tank, adequate protection against impact damage is to be provided.
5.2.26			JSP 317	The Road Tanker Delivery Stand must be impermeable to hydrocarbons and be capable of withstanding the axle weight of a fully laden delivery tanker.
5.2.27			JSP 317	The Road Tanker Delivery Stand. Delivery stand gradients and perimeter drains shall be designed to accept a discharge rate of / 16 litres per second for a period of 7 minutes over a 2m wide section of catchment channel, without overflowing.					FGSR Note: / NA in Germany where host nation standards take precedence.
5.2.28			APEA / Para 13.3.1	Vehicle Filling Area. Areas that are liable to contamination, such as the vehicle filling area, should be impermeable to all hydrocarbons and should not allow seepage through or below the surface. Areas such as these should always be protected at the perimeter by a suitable means of restraint such as kerbing, drainage channels or walling, to prevent the flow of contaminants towards permeable surfaces.
5.2.29			JSP 317	The following ‘Disconnect the Hose’ sign must be displayed at tanker Receipt/Issue points. The sign must be visible from the vehicle cab when the dispensing hose is connected to the installation:
5.2.30			JSP 317	The installation should have an effective means of both raising the alarm and giving warning in case of fire. It should be audible to all those likely to be effected by the fire. There must be access to a phone with in reasonable distance, which is to be clearly signposted.
5.2.31			APEA / Para 4.4.5	Vent pipes for underground storage tanks must be a minimum of 4 m above ground level (5m for non-emission control systems). The vent discharge point on an emissions control system should not be within 3 m of opening windows in any direction or any other opening to a building. In addition, vent pipes should not be located within 2 m of the installation boundary (3 m for non-emission control systems).
5.2.32			JSP 317	If a vapour recovery system is fitted a sign stating “Connect vapour line before off-loading ” must be displayed at each vapour return hose connection point.
5.2.33			JSP 317	If a vapour recovery system is fitted a sign stating “Warning, this tank is manifolded. Isolate tank vent pipe before commencing any work” must be displayed at each tank connected to a common vapour collection point.
5.2.34			JSP 317	The following Hazard Warning Sign stating “Petroleum Spirit, Highly Flammable, No Smoking or Naked Flames, No Mobile Phones, Switch Off Engine” must be displayed on all approaches to the facility in the local language and English:
5.2.35			JSP 317	The following minimised sign stating “Petroleum Spirit, Highly Flammable, No Smoking or Naked Flames, No Mobile Phones, Switch Off Engine” must be displayed at each metering pump/dispenser, the control point and offset filling point (If applicable) in the local language and English:
5.2.36			JSP 317	If any of the storage tanks have contained leaded petrol a label reading “This tank has contained leaded petroleum spirit. It must not be entered unless the prescribed regulations are complied with.” must be displayed at the opening of the tank.
5.2.37			D&MG 14 / Para 4.2 a	The centre lines of any tank openings or offset filling points are not to be within 4 m from roads, occupied buildings or the installation boundary. Where a building is a domestic premises or premises housing vulnerable populations, e.g. schools, hospitals, an increased separation distance of up to 12 m is recommended.
5.2.38			D&MG 14 / Para 4.2 b	Pipe work from tanks to offset filling points is to be routed below ground and in such a manner that access can be achieved after installation.
5.2.39			D&MG 14 / Para 4.4	Metering pumps should be located in the open air where they can be adequately ventilated. The centre lines of the dispensing pumps must be a minimum of 9m from living accommodation, 6m from other occupied buildings, including the control room and must not be within 4m of access roads or the installation boundary or any access roads.
5.2.40			D&MG 14 / 13.2 h	At unattended installations the name and contact number of the person to be contacted in an emergency should be displayed in an area adjacent to the emergency telephone.
5.2.41			APEA / Para 9.6.8	All unattended self-service (USS) sites must have the nozzle trigger latching mechanisms removed or disarmed. In addition the dispensing area(s) and position(s) of any emergency equipment should have adequate illumination.
5.2.42			D&MG 14 / Para 4.6	The Control Point at attended Installations should be located where the operator can provide supervision over fuelling activities. The view must not be obstructed by other buildings, structures or by a road tanker positioned for a fuel delivery.
5.2.43			D&MG 14 / Para 4.7	Interceptor vent pipes must extend to a minimum of 2.4 m above ground level and must not be within 3 m of access roads or building apertures.					FGSR Note: Vent pipes in Germany must be Stadt approved and may be less than 2.4m.
5.2.44			D&MG 14 / Para 6.1 c	All Tank vent pipes should be identified by their associated tank number.
5.2.45			D&MG 14 / Para 6.1 c	All fill/receipt points should be identified with the number, fuel type and capacity of the associated tank.
5.2.46			APEA / Para 11.6	Tank Contents Measurement Method. All tanks or compartments should be provided with a means of ascertaining the quantity of fuel stored. This may be by use of a dipstick or by some means of tank contents gauge. Indicate which method is used in the remarks column.					Manual Dip* / Auto Tank Gauge* / *Delete as applicable
5.2.47			D&MG 14 / Para 6.4 d	The storage tanks are fitted with overfill prevention devices or the unit have adopted a suitable operating procedure to prevent overfilling.
5.2.48			D&MG 14 / Para 6.7 a	For petrol installations the tank vent pipe is to be fitted above ground with a flame arrestor, designed to BS 7244.
5.2.49			D&MG 14 / 9.3 b	The mains electric incoming switch must be labelled “MAINS ISOLATING SWITCH”.
5.2.50			D&MG 14 / 9.3 g	Supplies to AFDS, Wet Stock Management (WSM) systems and leak detection systems must be fed by individual dedicated circuits. Miniature circuit breakers feeding such circuits are to be clearly labelled. “DO NOT SWITCH OFF”.
5.2.51			2.5.20 / D&MG 14 / 9.3 h	Emergency switching. The emergency (Fireman’s) switch to disconnect all pumps/dispensers and their associated equipment from the installation should be clearly identified with a sign stating “FUEL PUMPS SWITCH OFF HERE”. In order to comply with the Disability Discrimination Act 1995, when the installation is unattended, the emergency switch must be installed in a location which is accessible to all installation operators.
5.2.52			D&MG 14 / 9.5 r	A permanent label is to be fitted at all earthing and bonding connection points stating “SAFETY ELECTRICAL CONNECTION – DO NOT REMOVE”
5.2.53			DMG 14 / Para 11 b	If a canopy is fitted the minimum height from the ground to the underside of the lowest part of the canopy is to be 5.3m.					FGSR Note: The max height sign may be less than 5.3m however the actual height of the canopy should be an additional 1m.

5.3 FIRE, HEALTH & SAFETY					GRADING
					G				R			N/A		Remarks
Ref
5.3.1	JSP 317				Above ground storage tanks are to be marked with the correct NATO Product and Grade Identification markings. These markings must be visible from all directions.
5.3.2	JSP 317				Above ground Class I tanks shall be marked with ‘Highly Flammable, No Smoking, No Naked Lights’.
5.3.3	JSP 317				Above ground Class II tanks shall be marked ‘Flammable Liquid, No Smoking, No Naked Lights’.
5.3.4	JSP 317				Washing & changing facilities are to be provided for personnel at the place of work. In addition, the following items must also be provided: / Barrier Cream and After Work Cream. / Eyewash (In Date). / Emergency First Aid Kit.
5.3.5	JSP 317				Appropriate Personal Protective Equipment (PPE) and Respiratory Protective Equipment (RPE) is provided and used by all operators.
5.3.6	JSP 317				An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan
5.3.7	JSP 317				If the installation is unmanned i.e. it has a Ground Fuel Management System (GFMS), a telephone must be provided. If the installation is manned the attendant must know the location of the nearest telephone.
5.3.8	JSP 317				Fire Safety Notices & Fire Action Notices must be displayed in order to comply with the Health and Safety (Safety Signs and Signals) Regulations 1996. Locations and quantities should relate to the local risks and be the result of a risk assessment.
5.3.9	JSP 317				Smoking or Smoking materials are not permitted in the hazardous area. Personnel are to deposit any smoking materials in a safe designated contraband area before entering a hazardous zone or likely hazardous area.
5.3.10	JSP 317				A high standard of cleanliness is to be maintained at the installation. Rubbish of any kind must not be allowed to accumulate, and the growth of vegetation is to be controlled so as not to present a fire hazard.
5.3.11	JSP 317				Grass and Vegetation is to be cut back to a minimum of 15m. Isolated deciduous trees are permitted but conifers must be removed. Grass cutting and removal of vegetation must be carried out iaw the MoD Safety Rules and Procedures for Work on Petroleum installations.
5.3.12	JSP 317				The quantity and location of Fire Fighting apparatus will be determined by the Unit Fire Officer, however as a minimum requirement 2 x 9 Ltr Foam extinguishers should be provided for the first four dispense pumps. An additional extinguisher will be required for each additional two pumps.					4 = 2 10 = 5 / 5 = 2 11 = 5 / 6 = 3 12 = 6 / 7 = 3 13 = 6 / 8 = 4 14 = 7 / 9 = 4 15 = 7

5.4 ENVIRONMENTAL PROTECTION					GRADING
					G					R			N/A		Remarks
Ref
5.4.1		JSP 317			Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
5.4.2		JSP 317			A Pollution Control Point (PCP) should be established close to the MTFI. In addition to the Pollution Control Sorbents (PCS) which are held within the PCP, the following additional items should also be held: / Dustpan and Brush. / Stiff Broom. / Heavy duty plastic sacks and ties.
5.4.3		JSP 317			The unit must hold and maintain a local Spillage Register. All spillages are to be recorded and the forwarded to the Pollution Control Officer (PCO), who will collate the establishments, combined spill data.
5.4.4		Example USRP			Spillage Immediate Action Posters are to be prominently displayed at all Pollution Control Points and locations were F&L is stored.

5.5 OPERATING PROCEDURES					GRADING
					G				R			N/A		Remarks
Ref
5.5.1		JSP 317			When new deliveries of fuel are receipted into storage, the bulk tank contents shall be allowed to settle for a minimum of 2 hrs before any fuel is issued, providing the fuel is filtered into storage. If fuel is filtered into and out of storage i.e a BFCV and Installations filtration systems, no settling period is required.
5.5.2		JSP 317			Every effort is to be made to eliminate water from fuel storage tanks. The following applicable procedures should be followed to ensure water is kept to a minimum: / Tanks fitted with automatic water detection and ATG are to be checked once a month / Tanks with ATG are to be checked for water once a week. / Tanks without ATG are to be checked whenever the tank contents are dipped i.e daily
5.5.3		JSP 317			Security. When not in use, all manhole covers, dip hatch covers, outlet points and dipsticks are to be locked. Keys are to be held in safe custody under local arrangements. This requirement may be waivered by the Fuels Officer in Charge if the dipsticks and sampling hatches are located inside a secure building.
5.5.4		JSP 317			Bottled LPG: It is possible to store a small amount of LPG at the MTFI providing the following criteria is met: / Maximum permitted quantity is 400Kg irrespective of whether the cylinders are full or empty. / The LPG storage should not adversely affect the safety of the site. / The cylinders must be secured in a metal cage positioned in the open air.
5.5.5		JSP 317			Facilities for hand washing should be available within a reasonably practicable distance within reasonable distance. New installations should be provided with a hand wash basin.

6.	OIL FUEL DEPOT (OFD) & PETROLEUM STORAGE DEPOT (PSD)

STORAGE TANKS
Tank / No.	Capacity	Product	Above/ / Below Ground	Construction / (GRP/Steel-Double/Single Skin)	Integrally Bunded	Redundant	Decommissioned	Remarks

METERING/DISPENSE PUMPS
Pump / No.	Serial No	Make	Product	Remarks

INTERCEPTORS
Int No.	Construction (GRP/Brick/Steel)	Max Capacity (Ltrs)	Type (Full Retention or Bypass)	Class (1 or 2)	Remarks

ANY ADDITIONAL INFORMAT ION
PETROLEUM STORAGE DEPOT (PSD) OIL FUEL DEPOT (OFD)
6.1 INSTALLATION MAINTENANCE DOCUMENTATION					GRADING
					G		R	N/A		Remarks
Ref
6.1.1		DIO Practitioner Guide / PG 06/12			Inspection of the Fuel Infrastructure and Flammable Goods Facilities (Previously known as Task 249) : / An Inspection of the Fuel Infrastructure and Flammable Goods Facilities was carried out on _____________. A Certificate of Fitness for Continued Use was Issued for a period of _____ months . If the facility was considered ‘Not Fit For Continued Use’ or the unit were given a specified timeframe to rectify observations in the ‘Table of Defects’, which has lapsed without rectification, grade this question as Red and answer the following ‘Action Plan’ question. / *If this question is graded Red, answer the following Action Plan question.					FGSR Note: / Regulation – Condition of Certification / KPI
6.1.2		As above.			Inspection of the Fuel Infrastructure and Flammable Goods Facilities Action Plan (If applicable): / An Action Plan has been produced and funding has been allocated to rectify the specific observations detailed in the ‘Table of defects’ which warranted the ‘Not Fit for Continued Use’ grading.					*If green, send copy with completed report
6.1.3		DIO Practitioners Guide / PG 05/12 (Previously DWFS 7) / Para 6.5.3			Electrical Systems Test (Annual): / The Installations Electrical System was tested iaw the requirements of PG 05/12 on ____________ and was graded as ‘Satisfactory’. (An ‘Unsatisfactory’ grade should be awarded ‘Red’ for this question.) / If this question is graded Red, answer the following Electrical Test Action Plan question.					FGSR Note: / Regulation – Condition of Certification / KPI
6.1.4		As above			Electrical Systems Test Action Plan (If applicable): / An Action Plan has been produced and funding has been allocated to rectify the specific observations which resulted in the ‘Unsatisfactory’ Electrical Test grading.					*If green, send copy with completed report
6.1.5		JSP 317			Lightning Protection (If applicable) / If the installation is located in an area susceptible to lightning / BS 6651 and BS EN 62305 are to be consulted to determine whether lightning protection is required. If it is required, protection installed at installations constructed prior to 31 Aug 08 is to be maintained iaw the requirements of BS 6651 until such time that the installation is upgraded, after which BS EN 62305 will apply. Lightning protection installed on or after 31 Aug 08 is to be installed and maintained iaw the requirements of BS EN 62305.
6.1.6		PG 05/12 / Job 2.2.2			Storage tanks: / Visually check exterior of storage tanks including associated equipment on 3 monthly basis. Last inspected____________.
6.1.7		PG 05/12 / Job 2.2.3			Tank manholes must be stamped with the following: / Date of last inspection/cleaning / Carried out by / Date of next inspection
6.1.8		PG 05/12 / Job 8.1			Pumps have been maintained iaw manufacturers recommendations every 3 months and inspected for correct operation on a 6 monthly basis.
6.1.9		PG 05/12 / Job 7.2			Flow meter accuracy has been checked and details have been recorded in the local maintenance log (annually)
6.1.10		PG 05/12 / Job 5.2			Pipelines/work pressure have been tested at the prescribed intervals to 150% of normal working pressure. (36 month intervals)
6.1.11		JSP 317 / Paras 2.9.08 & / 2.9.13 / EA PPG 3			Oil Water Interceptor (OWI) Design: / The OWI should meet the following specifications: / Minimum capacity of 7600 litres; and greater than the smallest compartment of the delivery tanker. / Full retention / Class 1 (if draining to Surface or Foul Water) or Class 2 (if draining to Foul Water only) / If it does not meet the above conditions, and an Environmental Risk Assessment has not been produced to mitigate this risk, a ‘Red’ grade must be awarded for this question. / If an Environmental Risk Assessment has been produced; which mitigates the design shortcomings, this question can subsequently be graded as Green. / If the OWI does not meet the above specifications; answer the following mitigation question below.					KPI
6.1.12	JSP 317			OWI Mitigation - Pollution ERA: / A Pollution ERA, which has been updated within the previous 12 months, has been produced to mitigate the increased risk created by the inadequate OWI design. / If the Pollution ERA mitigates the inadequate OWI design by demonstrating a solution that is equivalent or better than the protection afforded by a suitable OWI, subsequent assessments can be assessed as Green.
6.1.13	JSP 317			OWI Maintenance: These assets are maintained under Project Aquatrine by Aquatrine Service Providers. As a minimum, every 6 months or iaw manufacturers’ instructions, OWIs should be physically inspected to: / Ensure the Integrity of OWI / Identify the quantity of any accumulated F&L and silt. / Confirm that all electrical equipment is functioning correctly i.e Alarms. / Inspect the Condition of any coalescing devices and replace if necessary. / There must be evidence to clearly demonstrate that all the above points have been completed for this serial to be graded compliant. / The last inspection of the Interceptor was conducted by ___________ on ___________. If this date exceeds 6 months or the date of the last inspection cannot be ascertained award a ‘Red’ grade for this question.					FGSR Note: The Aquatrine contract only includes mainland UK units. In all other instances host nation standards will apply. / KPI

6.2 OPERATION & FUNCTION					GRADING
					G		R	N/A		Remarks
Ref
6.2.1		JSP 317			All primary pipe work is to be identified at every junction, valve, pump, separator, monitor and ground penetration with the relevant colour coded band in accordance with Defence Standard 05-52 (Part 2). In addition arrows should be displayed on all pipe work to identify the direction of flow.
6.2.2		JSP 317			Each direct fill or offset fill point is to be marked with its associated tank or compartment number and fuel type. The markings are to be as close as possible to the road tankers delivery hose connection point.
6.2.3		JSP 317			The installation should have an effective means of both raising the alarm and giving warning in case of fire. It should be audible to all those likely to be effected by the fire. A telephone must be provided at the facility.
6.2.4		JSP 317			An effective means of communication should be provided between personnel involved in the loading/unloading operations, and other parts of the site such as the control room. If radios are used they must be suitably rated for use in the hazardous area.
6.2.5		JSP 317			The changing or removal of clothing which has been splashed with F&L products is prohibited in the hazardous area. Clothing contaminated with IP Class I or II products should only be removed after saturating with water from a drench shower which is to be sited in the vicinity of the receipt/issue point. If no drench shower is provided a risk assessment is to be produced to identify an alternative means of saturation.
6.2.6		JSP 317			Above Ground Storage Tanks- Secondary Containment The bund wall must be capable of retaining 110% of the largest container within the bund or 25% of the aggregate of multiple containers, whichever is greater.
6.2.7		JSP 317			Above Ground Storage Tanks- Secondary Containment The bund wall must: / Be impervious to liquid / Not normally be higher than 1.5m high. / Be fitted with crash protection if susceptible to impact damage e.g adjacent to a vehicle manoeuvring area.
6.2.8		JSP 317			Above Ground Storage Tanks- Secondary Containment. In order to prevent jetting; a phenomenon caused when the primary container fails and F&L is propelled at force beyond the secondary containment, the bund wall is not to be constructed too close to the tank.
6.2.9		JSP 317			Above Ground Storage Tanks - Secondary Containment The bund base and walls must not be penetrated by any valve, pipe or other opening which is used for draining the bund. Where a tank fill or draw off pipe must pass through the bund base or wall, the hole must be carefully sealed with a fire resistant seal to prevent oil escaping.
6.2.10		JSP 317			Above Ground Storage Tanks - Secondary Containment Rainwater which collects in the sump must be removed on a regular basis to ensure the bund capacity is maintained. This water is to be disposed of appropriately to ensure no pollution occurs.
6.2.11		JSP 317			Inspection of Bunds - Bunds should be regularly inspected for signs of damage and checked for water by the operator on a weekly basis.
6.2.12		HSG 176 / Para 104			Pumps are potential ignition sources and should be located outside the bund, on an impervious base, preferably in the open air. The minimum recommended safety distance from buildings, boundaries and sources of ignition is 7.5m for a large standard pump, however this can be reduced to 3m if the pumps capacity is <100m3/ hr.
6.2.13		HSG 176 / Para 151			The bund should not be used for the storage of flammable liquid containers, gas cylinders (full or empty) or other hazardous substances.
6.2.14		2.8.21			Above Ground Storage Tanks - Secondary Containment If oil or a mixture of oil and water is found in the bund it must be disposed of in accordance with current Hazardous Waste Regulations.
6.2.15		Oil Storage Regs 3 (3)			Above Ground Storage Tanks- Secondary Containment Valves should be as resistant to unauthorised interference and vandalism as far as is feasibly possible, with lockable or removable hand wheels.
6.2.16		OSR 01 / Reg 3(3)			Above Ground Storage Tank- Secondary Containment All tank vent pipes, valves, filters, sight gauges and any other ancillary equipment with the exception of the fill pipe, draw off pipe or pump if the fuel has a flashpoint of less than 32ºc, must be positioned within the bund wall.
6.2.17		OSR 01 / Reg 3(3)			Above Ground Storage Tanks Valves should be marked to indicate whether they are open or closed, kept locked when not in use and fitted with a blanking cap or plug.
6.2.18		JSP 317			Above Ground Storage Tanks - Separation distances for ‘small’ tanks. A small tank is considered to be a tank with a diameter of less than 10m. The minimum separation distances from site boundaries, fixed sources of ignition, buildings and process areas for single small tanks are as follows: / Tank Capacity (m³) Separation (m) / Less than or equal to 1 1* / Greater than 1 and less than or equal to 5 4 / Greater than 5 and less than or equal to 33 6 / Greater than 33 and less than or equal to 100 8 / Greater than 100 and less than or equal to 250 10 / Greater than 250 15 / *In this instance the tank must be sited at least 2m from doors, plain glazed windows, other openings or means of escape. In addition they must not be below any openings from an upper floor, regardless of vertical distance.

6.2.19		JSP 317			Above Ground Storage Tanks - Separation distances for groups of ‘small’ tanks . For the purpose of determining the safe separation distances from site boundaries, buildings, process areas and fixed sources of ignition a group of small tanks may be regarded as one tank. The minimum distances for such tanks are as follows: / Tank Capacity (m³) Separation (m) / Less than or equal to 3 1* / Greater than 3 and less than or equal to 15 4 / Greater than 15 and less than or equal to 100 6 / Greater than 100 and less than or equal to 300 8 / Greater than 300 and less than or equal to 750 10 / Greater than 750 and less than or equal to 8000 15 / *In this instance the tank must be sited at least 2m from doors, plain glazed windows, other openings or means of escape. In addition they must not be below any openings from an upper floor, regardless of vertical distance.
6.2.20		JSP 317			Electrical installations must be designed, installed and maintained in accordance with the current construction standards and comply with the hazardous area in which they are located.					FGSR Note: / Regulation
6.2.21		JSP 317			All metal parts of the installation should be bonded together and earthed to prevent the accumulation of electrostatic charge.
6.2.22		JSP 317			A schematic diagram showing the installation layout and valve numbering is to be mounted and displayed in a prominent position in the pump house or other suitable location at the installation.
6.2.23		JSP 317			All installation valves are to be numbered using a disc no smaller than 100 mm in diameter. All valves must correspond exactly with the information provided on the schematic.
6.2.24		JSP 317			Security. When not in use, all manhole covers, dip hatch covers, outlet points and dipsticks are to be locked. Keys are to be held in safe custody under local arrangements.
6.2.25		JSP 317			To prevent trespassing or tampering storage areas are to be enclosed by a substantial fence of at least 1.8m high, constructed of welded mesh or chain link.
6.2.26		JSP 317			The installation has an integral Full Retention Separator/Oil Water Interceptor (OWI) which offers sufficient environmental protection to the surrounding area.
6.2.27		JSP 317			The OWI must be fitted with a high-level alarm & automatic shut off valve.
6.2.28		JSP 317			The Road Tanker Delivery Stand should be located in a safe, well ventilated position in the open and should offer a clear, unobstructed forward escape route.
6.2.29		JSP 317			The Road Tanker Delivery Stand – Attended. Prior to a bulk receipt at an attended installation, the delivery driver must be presented with a notice detailing safe delivery/receipt and emergency procedures. The driver is to read and sign the notice to confirm they understand the procedures before commencing delivery.
6.2.30		JSP 317			The minimum recommended distance of a Road Tanker Delivery Stand from occupied buildings, the site boundary or a fixed source of ignition is 10m or the distance calculated on the DSEAR RA; whichever is greater. This does not apply to Bulk Waste, UETF, FFO and Domestic Heating Tanks.					KPI
6.2.31		JSP 317			The Road Tanker Delivery Stand. The delivery stand should be a minimum of 15m x 5m. If this isn’t practicable, signage and barriers are to be used to restrict vehicle and personnel access during transfer operations.
6.2.32		JSP 317			The Road Tanker Delivery Stand. Road tankers shall not be made to wait on public or internal busy roads. The delivery stand should be substantially level to ensure full extraction during deliveries.. If the delivery stand is in close proximity to an above ground storage tank, adequate protection against impact damage is to be provided.
6.2.33		JSP 317			The Road Tanker Delivery Stand must be impermeable to hydrocarbons and be capable of withstanding the axle weight of a fully laden delivery tanker.
6.2.34		JSP 317			The following ‘Disconnect the Hose’ sign must be displayed at tanker Receipt/Issue points. The sign must be visible from the vehicle cab when the dispensing hose is connected to the installation:
6.2.35		JSP 317			In addition to the Road Tanker Delivery Stand, traffic areas should also be impermeable to hydrocarbons and be capable of holding any spilled residue until such time as the drainage system can accept and convey the spillage to the OWI.
6.2.36		JSP 317			Roadways shall be laid out to provide easy access to and from all parts of the installation. A one-way traffic system should be adopted whenever possible, particularly in areas where vehicles are loaded and unloaded.
6.2.37		JSP 317			Roads shall be designed to enable all-weather access to tanks for fire-fighting purposes. Where 2-way traffic is encountered the width of the road shall be sufficient to allow 2 vehicles to pass. Single-track roads shall be provided with lay-byes. Curvatures, contours, bearing strengths, junctions and clearance heights shall accommodate the largest vehicles, including emergency vehicles, likely to use the roads.
6.2.38		JSP 317			Working areas associated with storage tanks, including loading and unloading points, should be adequately lit when in use. An average luminance of at least 50 lux is recommended at ground level, on stairs at access platforms etc. It may be necessary to increase this to 100 lux where perception of detail is required, for example to read level gauges.
6.2.39		JSP 317			Bonding. Aviation bulk fuel dispense and receipt points shall be provided with a bonding cable. The bonding cable shall be connected to the fixed earth network, which in turn will be connected to the dispense/ receipt pipeline.
6.2.40		JSP 317			The following Hazard Warning Sign must be displayed on all approaches to the facility in the local language and English:
6.2.41		JSP 317			A high standard of cleanliness is to be maintained at the installation. Rubbish of any kind must not be allowed to accumulate, and the growth of vegetation is to be controlled so as not to present a fire hazard.

6.3 FIRE, HEALTH & SAFETY					GRADING
					G		R		N/A		Remarks
Ref
6.3.1			JSP 317	Above ground storage tanks are to be marked with the correct NATO Product and Grade Identification markings. These markings must be visible from all directions.
6.3.2			JSP 317	Class I tanks shall be marked with ‘Highly Flammable, No Smoking, No Naked Lights’.
6.3.3			JSP 317	Class II tanks shall be marked ‘Flammable Liquid, No Smoking, No Naked Lights’.
6.3.4			JSP 317	Washing & changing facilities are to be provided for personnel at the place of work. In addition, the following items must also be provided: / Barrier Cream and After Work Cream. / Eyewash (In Date). / Emergency First Aid Kit.
6.3.5			JSP 317	Appropriate Personal Protective Equipment (PPE) and Respiratory Protective Equipment (RPE) is provided and used by all operators.
6.3.6			JSP 317	The quantity and location of all fire fighting equipment, which is determined by the Unit Fire Officer, must reflect what is stated in the Fire Safety Risk Assessment (FSRA).
6.3.7			JSP 317	An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan
6.3.8			JSP 317	Fire Safety Notices & Fire Action Notices must be displayed in order to comply with the Health and Safety (Safety Signs and Signals) Regulations 1996. Locations and quantities should relate to the local risks and be the result of a risk assessment.
6.3.9			JSP 317	Smoking or Smoking materials are not permitted in the hazardous area. Personnel are to deposit any smoking materials in a safe designated contraband area before entering a hazardous zone or likely hazardous area.
6.3.10			HSG 176 / Para 151		Combustible material such as vegetation, litter or rubbish should not be allowed to accumulate in the bund as this will increase the risk of fire.
6.3.11			JSP 317		Grass and Vegetation is to be cut back to a minimum of 15m. Isolated deciduous trees are permitted but conifers must be removed. Grass cutting and removal of vegetation must be carried out iaw the MoD Safety Rules and Procedures for Work on Petroleum installations.

6.4 ENVIRONMENTAL PROTECTION					GRADING
					G	R			N/A		Remarks
Ref
6.4.1			JSP 317	Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
6.4.2			JSP 317	A Pollution Control Point (PCP) is to be established at the installation. The PCP must be clearly identifiable, stocked appropriately and be maintained on a regular basis.
6.4.3			JSP 317	The unit must hold and maintain a local Spillage Register. All spillages are to be recorded and the forwarded to the Pollution Control Officer (PCO), who will collate the establishments, combined spill data.
6.4.4			Example USRP	Spillage Immediate Action Posters are to be prominently displayed at all Pollution Control Points and locations were F&L is stored.

6.5 OPERATING PROCEDURES					GRADING
					G		R		N/A		Remarks
Ref
6.5.1			JSP 317	Elimination of Water from Storage Tanks. / The presence of water in storage tanks can give rise to microbiological contamination, and the leaching out of additives. Every effort is to be made to eliminate water in storage tanks. To ensure that water in fuel tanks is kept to a minimum, the following procedures are to be applied: / Tanks fitted with automatic water detection and an integrated water removal systems, or automatic tank gauges (ATG), compliant with STANAG 7011, are to be checked for water once a month. / Tanks fitted with an ATG, compliant with STANAG 7011, are to be checked for water once a week. Where the tank has not issued or received fuel during the previous week, or where local conditions preclude weekly water checks from being conducted, the frequency of checks may be extended to a period not exceeding one month. / Tanks which are not fitted with an ATG are to be checked for water whenever the tank contents are dipped. If water is detected in a tank that is not fitted with an automatic water detection system which incorporates an integrated water removal system, a works service request is to be raised for its immediate removal. The results of all water checks are to be recorded and stock adjustments made in accordance with DLF.
6.5.2			JSP 317	The following basic Quality Control measures are instigated at the installation: / Documentation is checked prior to receipt of any fuel to confirm correct product and grade is being delivered. / A sample is to be taken from the tanker prior to commencing receipt operations. Sample must be clear and free from suspended matter and water. / Observe proper maintenance procedures for all facilities. / Ensure the correct use and placement of filtration equipment.
6.5.3			JSP 317		Before any product is transferred into storage the following actions must be taken: / All storage tanks to be used must be suitable for the product and if empty, certified clean. If they contain product it must be of the same grade, free from contamination and within specification and retest date / All filters, connections and associated pipe work must be checked to ensure cleanliness, correct connection and operation. All hatches are to be secured to avoid the ingress of water and other contaminants.
6.5.4			JSP 317		When new deliveries of fuel are receipted into storage, the bulk tank contents shall be allowed to settle for a minimum of 2 hrs before any fuel is issued, providing the fuel is filtered into storage. If fuel is filtered into and out of storage i.e a BFCV and Installations filtration systems; in this instance no settling period is required.
6.5.5			DLF		Frequency of Dips / Daily. All In Use bulk fuel storage tanks and Bulk Fuel carrying Vehicles (BFCV), are to be dipped daily. This can be carried out by ATG (if accurate to +/- 1mm and +/- 0.5oC) or manually and, whenever possible before issues of the day. / Weekly. The dip, water check and temperature measurement (temperature is not required for BFCVs) of all bulk storage tanks, and BFCVs, including those where no fuel movement has taken place, is to be carried out once a week under the supervision of an authorised officer, normally Fridays. / Last Working Day of the Month. Dips are to be carried out on the last working day of the month, following the procedures at Paragraph 3b above and under the supervision of an authorised officer (OC Supply at RAF Units).
6.5.5			JSP 317		Turnover of Stocks / Stocks are always to be issued on the principle of using oldest stock first. The age of stock is to be assessed by the length of time it has been in storage in the installation. Where an installation has two or more tanks, the tanks are to be filled and emptied in rotation.

7.	AVIATION BULK FUEL INSTALLATIONS (BFI)

STORAGE TANKS

Tank No.	Capacity	Product	Above/ / Below / Ground	Construction / (GRP/Steel-Double/Single Skin)	Redundant	Decommissioned	Remarks

METERING/DISPENSE PUMPS

Pump / No.	Serial No.	Make	Product	Remarks

FILTER WATER SEPARATORS

FWS / No.	Serial No.	Coalescer Elements		Differential Pressure Gauge		Date Pressure Relief Valve Tested to 110%	Remarks
		Make	Date installed	Calibrated	Last Inspected

INTERCEPTORS

Int / No.	Construction / (GRP/Brick/Steel)	Max Capacity / (Ltrs)	Type / (Full Retention or Bypass)	Class / (1 or 2)	Remarks

AVIATION BULK FUEL INSTALLATION
7.1 INSTALLATION MAINTENANCE DOCUMENTATION
					G					R				N/A				Remarks
Note: BF(G) based units will be inspected under an alternative regime. DSA FGSR should be contacted for guidance when completing this section.
Ref
7.1.1	DIO Practitioner Guide / PG 06/12 (Previously PG 01/09)		Inspection of the Fuel Infrastructure and Flammable Goods Facilities (Previously known as Task 249) : / An Inspection of the Fuel Infrastructure and Flammable Goods Facilities was carried out on _____________. A Certificate of Fitness for Continued Use was Issued for a period of _____ months . If the facility was considered ‘Not Fit For Continued Use’ or the unit were given a specified timeframe to rectify observations in the ‘Table of Defects’, which has lapsed without rectification, grade this question as Red and answer the following ‘Action Plan’ question. / *If this question is graded Red, answer the following Action Plan question.					FGSR Note: / Regulation – Condition of Certification. / KPI
7.1.2	As above.		Inspection of the Fuel Infrastructure and Flammable Goods Facilities Action Plan (If applicable): / An Action Plan has been produced and funding has been allocated to rectify all observations highlighted in the Inspection of the Fuel Infrastructure and Flammable Goods Facilities, Table of defects
7.1.3	DIO Practitioners Guide / PG 05/12 (Previously DWFS 7) / Para 6.5.3		Electrical Systems Test (Annual): / The Installations Electrical System was tested iaw the requirements of PG 05/12 on ____________ and was graded as ‘Satisfactory’. (An ‘Unsatisfactory’ grade should be awarded ‘Red’ for this question.) / If this question is graded Red, answer the following Electrical Test Action Plan question.					FGSR Note: / Regulation – Condition of Certification
7.1.4	As above.		Electrical Systems Test Action Plan (If applicable): / An Action Plan has been produced and funding has been allocated to rectify the specific observations which resulted in the ‘Unsatisfactory’ Electrical Test grading.
7.1.5	JSP 317		Oil Water Interceptor (OWI) Design: / The OWI should meet the following specifications: / Minimum capacity of 7600 litres; and greater than the smallest compartment of the delivery tanker / Full retention / Class 1 (if draining to Surface or Foul Water) or Class 2 (if draining to Foul Water only) / If it does not meet the above conditions, and an Environmental Risk Assessment has not been produced to mitigate this risk, a ‘Red’ grade must be awarded for this question. / If an Environmental Risk Assessment has been produced; which mitigates the design shortcomings, this question can subsequently be graded as Green. / If the OWI does not meet the above specifications; answer the following mitigation question below.					FGSR Note: / NA in Germany where host nation standards take precedence. / KPI
7.1.6	JSP 317		OWI Mitigation - Pollution ERA: / A Pollution ERA, which has been updated within the previous 12 months, has been produced to mitigate the increased risk created by the inadequate OWI design. / If the Pollution ERA mitigates the inadequate OWI design by demonstrating a solution that is equivalent or better than the protection afforded by a suitable OWI, subsequent assessments can be assessed as Green.					FGSR Note: / NA in Germany where host nation standards take precedence.
7.1.7	JSP 317		OWI Maintenance: These assets are maintained under Project Aquatrine by Aquatrine Service Providers. As a minimum, every 6 months or iaw manufacturers’ instructions, OWIs should be physically inspected to: / Ensure the Integrity of OWI / Identify the quantity of any accumulated F&L and silt. / Confirm that all electrical equipment is functioning correctly i.e Alarms. / Inspect the Condition of any coalescing devices and replace if necessary. / There must be evidence to clearly demonstrate that all the above points have been completed for this serial to be graded compliant. / The last inspection of the Interceptor was conducted by ___________ on ___________. If this date exceeds 6 months or the date of the last inspection cannot be ascertained award a ‘Red’ grade for this question.					FGSR Note: / The Aquatrine contract only includes mainland UK units. In all other instances host nation standards will apply. / KPI
7.1.8	PG 05/12 / Job 2.2.2		Storage tanks: / Visually check exterior of storage tanks including associated equipment on 3 monthly basis. Last inspected____________.
7.1.9	PG 05/12 / Job 3.3		Storage Tank Contents Gauge: / Inspect external tank equipment gauges every 12 months. Last inspected_______
7.1.10	PG 05/12 / Job 2.2.3		Tank manholes must be stamped with the following: / Date of last inspection/cleaning / Carried out by / Date of next inspection
7.1.11	PG 05/12 / Job 8.2		FWS maintenance: / a) Monitoring the pressure differential across the unit. (3m) / b) Inspect unit for leaks, mechanical damage and corrosion. (6m) / c) Ensuring correct operation of unit. (6m) / d) Test automatic water drains (where fitted) in accordance with manufacturers approved original test procedure. (6m) / Note: Details of inspections and tests undertaken should be recorded in the maintenance register, together with dates of cartridge replacement – which should also be stencilled on the outside of the unit.
7.1.12	JSP 317		FWS Coalescer Element Replacement*: FWS elements should be changed when the differential Pressure (DP) across the filter exceeds 1 BAR (15 PSI) at (or corrected to) the maximum operating flow rate through the filter vessel or after 36 months, whichever occurs the soonest. / a) Elements installed* ________________. / b) Next change due @ 15 psi dp or _______________.					*Must not exceed 36 months
7.1.13	PG 05/12 / Job 9.1		Rubber hoses have been maintained as follows: / Visual Inspection for damage (3m) / Pressure tested (6m) / Electrical continuity tested (6m))
7.1.14	PG 05/12 / Job 8.1		Pumps have been maintained iaw manufacturers recommendations every 3 months and inspected for correct operation on a 6 monthly basis.
7.1.15	JSP 317		All meters associated with the storage media are to be in good working order and calibrated.
7.1.16	PG 05/12 / Job 7.2		Flow meter accuracy has been checked and details have been recorded in the local maintenance log (annually)
7.1.17	PG 05/12 / Job 7.3		Differential pressure gauges have been checked and details have been recorded in the local maintenance log (6m)
7.1.18	PG 05/12 / Job 5.2		Pipelines/work pressure have been tested at the prescribed intervals to 150% of normal working pressure. (36m)

7.2 OPERATION & FUNCTION					GRADING
					G					R					N/A		Remarks
Ref*
7.2.1	JSP 317		All primary pipe work is to be identified at every junction, valve, pump, separator, monitor and ground penetration with the relevant colour coded band in accordance with Defence Standard 05-52 (Part 2). In addition arrows should be displayed on all pipe work to identify the direction of flow.
7.2.2	JSP 317		Each direct fill or offset fill point is to be marked with its associated tank or compartment number and fuel type. The markings are to be as close as possible to the road tankers delivery hose connection point.
7.2.3	JSP 317		A telephone must be provided at the installation.
7.2.4	HSG 176 / Para 191		An effective means of communication should be provided between personnel involved in the loading/unloading operations, and other parts of the site such as the control room. If radios are used they must be suitably rated for use in the hazardous area.
7.2.5	JSP 317		The changing or removal of clothing which has been splashed with F&L products is prohibited in the hazardous area. Clothing contaminated with IP Class I or II products should only be removed after saturating with water from a drench shower which is to be sited in the vicinity of the receipt/issue point. If no drench shower is provided a risk assessment is to be produced to identify an alternative means of saturation.
7.2.6	JSP 317		Above Ground Storage Tanks- Secondary Containment The bund wall must be capable of retaining 110% of the largest container within the bund or 25% of the aggregate of multiple containers, whichever is greater.
7.2.7	JSP 317		Above Ground Storage Tanks- Secondary Containment The bund wall must: / Be impervious to liquid / Not normally be higher than 1.5m high. / Be fitted with crash protection if susceptible to impact damage e.g adjacent to a vehicle manoeuvring area.
7.2.8	JSP 317		Above Ground Storage Tanks- Secondary Containment. In order to prevent jetting; a phenomenon caused when the primary container fails and F&L is propelled at force beyond the secondary containment, the bund wall is not to be constructed too close to the tank.
7.2.9	JSP 317		Above Ground Storage Tanks - Secondary Containment The bund base and walls must not be penetrated by any valve, pipe or other opening which is used for draining the bund. Where a tank fill or draw off pipe must pass through the bund base or wall, the hole must be carefully sealed with a fire resistant seal to prevent oil escaping.
7.2.10	JSP 317		Above Ground Storage Tanks - Secondary Containment Rainwater which collects in the sump must be removed on a regular basis to ensure the bund capacity is maintained. This water is to be disposed of appropriately to ensure no pollution occurs.
7.2.11	JSP 317		Inspection of Bunds - Bunds should be regularly inspected for signs of damage and checked for water by the operator on a weekly basis.
7.2.12	HSG 176 / Para 104		Pumps are potential ignition sources and should be located outside the bund, on an impervious base, preferably in the open air. The minimum recommended safety distance from buildings, boundaries and sources of ignition is 7.5m for a large standard pump, however this can be reduced to 3m if the pumps capacity is <100m3/ hr.
7.2.13	HSG 176 / Para 151		The bund should not be used for the storage of flammable liquid containers, gas cylinders (full or empty) or other hazardous substances.
7.2.14	JSP 317		Above Ground Storage Tanks - Secondary Containment If oil or a mixture of oil and water is found in the bund it must be disposed of in accordance with current Hazardous Waste Regulations.
7.2.15	Oil Storage Regs 3 (3)		Above Ground Storage Tanks- Secondary Containment Valves should be as resistant to unauthorised interference and vandalism as far as is feasibly possible, with lockable or removable hand wheels.
7.2.16	OSR 01 / Reg 3(3)		Above Ground Storage Tank- Secondary Containment All tank vent pipes, valves, filters, sight gauges and any other ancillary equipment with the exception of the fill pipe, draw off pipe or pump if the fuel has a flashpoint of less than 32ºc, must be positioned within the bund wall.
7.2.17	OSR 01 / Reg 3(3)		Above Ground Storage Tanks Valves should be marked to indicate whether they are open or closed, kept locked when not in use and fitted with a blanking cap or plug.
7.2.18	JSP 317		Above Ground Storage Tanks - Separation distances for ‘small’ tanks. A small tank is considered to be a tank with a diameter of less than 10m. The minimum separation distances from site boundaries, fixed sources of ignition, buildings and process areas for single small tanks are as follows: / Tank Capacity (m³) Separation (m) / Less than or equal to 1 1* / Greater than 1 and less than or equal to 5 4 / Greater than 5 and less than or equal to 33 6 / Greater than 33 and less than or equal to 100 8 / Greater than 100 and less than or equal to 250 10 / Greater than 250 15 / *In this instance the tank must be sited at least 2m from doors, plain glazed windows, other openings or means of escape. In addition they must not be below any openings from an upper floor, regardless of vertical distance.

7.2.19	JSP 317		Above Ground Storage Tanks - Separation distances for groups of ‘small’ tanks . For the purpose of determining the safe separation distances from site boundaries, buildings, process areas and fixed sources of ignition a group of small tanks may be regarded as one tank. The minimum distances for such tanks are as follows: / Tank Capacity (m³) Separation (m) / Less than or equal to 3 1* / Greater than 3 and less than or equal to 15 4 / Greater than 15 and less than or equal to 100 6 / Greater than 100 and less than or equal to 300 8 / Greater than 300 and less than or equal to 750 10 / Greater than 750 and less than or equal to 8000 15 / *In this instance the tank must be sited at least 2m from doors, plain glazed windows, other openings or means of escape. In addition they must not be below any openings from an upper floor, regardless of vertical distance.
7.2.20	JSP 317		Electrical installations must be designed, installed and maintained in accordance with the current construction standards and comply with the hazardous area in which they are located.					FGSR Note: / Regulation – Condition of Certification.
7.2.20	JSP 317		All metal parts of the installation should be bonded together and earthed to prevent the accumulation of electrostatic charge.
7.2.22	JSP 317		A schematic diagram showing the installation layout and valve numbering is to be mounted and displayed in a prominent position in the pump house or other suitable location at the installation.
7.2.23	JSP 317		All installation valves are to be numbered using a disc no smaller than 100 mm in diameter. All valves must correspond exactly with the information provided on the schematic.
7.2.24	JSP 317		Security. When not in use, all manhole covers, dip hatch covers, outlet points and dipsticks are to be locked. Keys are to be held in safe custody under local arrangements.
7.2.25	JSP 317		To prevent trespassing or tampering storage areas are to be enclosed by a substantial fence of at least 1.8m high, constructed of welded mesh or chain link.
7.2.26	JSP 317		The installation has an integral Full Retention Separator/Oil Water Interceptor (OWI), which offers sufficient environmental protection to the surrounding area.					FGSR Note: Host nation standards take precedence in Germany.
7.2.27	JSP 317		The OWI must be fitted with a high-level alarm & automatic shut off valve.					FGSR Note: As above.
7.2.28	JSP 317		The Road Tanker Delivery Stand should be located in a safe, well ventilated position in the open and should offer a clear, unobstructed forward escape route.					FGSR Note: / Regulation – Condition of Certification.
7.2.29	JSP 317		The Road Tanker Delivery Stand – Attended. Prior to a bulk receipt at an attended installation, the delivery driver must be presented with a notice detailing safe delivery/receipt and emergency procedures. The driver is to read and sign the notice to confirm they understand the procedures before commencing delivery.
7.2.30	JSP 317		The minimum recommended distance of a Road Tanker Delivery Stand from occupied buildings, the site boundary or a fixed source of ignition is 10m or the distance calculated on the DSEAR RA; whichever is greater. This does not apply to Bulk Waste, UETF, FFO and Domestic Heating Tanks.					KPI
7.2.31	JSP 317		The Road Tanker Delivery Stand. The delivery stand should be a minimum of 15m x 5m. If this isn’t practicable, signage and barriers are to be used to restrict vehicle and personnel access during transfer operations.
7.2.32	JSP 317		The Road Tanker Delivery Stand. Road tankers shall not be made to wait on public or internal busy roads. The delivery stand should be substantially level to ensure full extraction during deliveries.. If the delivery stand is in close proximity to an above ground storage tank, adequate protection against impact damage is to be provided.
7.2.33	JSP 317		The Road Tanker Delivery Stand must be impermeable to hydrocarbons and be capable of withstanding the axle weight of a fully laden delivery tanker.
7.2.34	JSP 317		The following ‘Disconnect the Hose’ sign must be displayed at tanker Receipt/Issue points. The sign must be visible from the vehicle cab when the dispensing hose is connected to the installation:
7.2.35	JSP 317		In addition to the Road Tanker Delivery Stand, traffic areas should also be impermeable to hydrocarbons and be capable of holding any spilt residue until such time as the drainage system can accept and convey the spillage to the OWI.
7.2.36	JSP 317		The drainage system shall be designed to minimise the surface area of any / spillage, and be isolated from surface water drainage systems. In remote sites on non-MoD owned land (such as SAR refuelling sites), where an OWI cannot be installed, an environmental risk assessment must be completed for the delivery, storage and issue of fuel. The appropriate duty holder must accept any residual risk, and the USRP must make specific reference to such sites.
7.2.37	JSP 317		Roadways shall be laid out to provide easy access to and from all parts of the installation. A one-way traffic system should be adopted whenever possible, particularly in areas where vehicles are loaded and unloaded.
7.2.38	JSP 317		Roads shall be designed to enable all-weather access to tanks for fire-fighting purposes. Where 2-way traffic is encountered the width of the road shall be sufficient to allow 2 vehicles to pass. Single-track roads shall be provided with lay-byes. Curvatures, contours, bearing strengths, junctions and clearance heights shall accommodate the largest vehicles, including emergency vehicles, likely to use the roads.
7.2.39	JSP 317		Working areas associated with storage tanks, including loading and unloading points, should be adequately lit when in use. An average luminance of at least 50 lux is recommended at ground level, on stairs at access platforms etc. It may be necessary to increase this to 100 lux where perception of detail is required, for example to read level gauges.
7.2.40	JSP 317		Bonding. Aviation bulk fuel dispense and receipt points shall be provided with a bonding cable. The bonding cable shall be connected to the fixed earth network, which in turn will be connected to the dispense/ receipt pipeline.
7.2.41	JSP 317		The following Hazard Warning Sign must be displayed on all approaches to the facility in the local language and English:
7.2.42	JSP 317		A high standard of cleanliness is to be maintained at the installation. Rubbish of any kind must not be allowed to accumulate, and the growth of vegetation is to be controlled so as not to present a fire hazard.

7.3 FIRE, HEALTH & SAFETY					GRADING
					G					R		N/A				Remarks
Ref
7.3.1	JSP 317	Above ground storage tanks are to be marked with the correct NATO Product and Grade Identification markings. These markings must be visible from all directions.
7.3.2	JSP 317	Class I tanks shall be marked with ‘Highly Flammable, No Smoking, No Naked Lights’.
7.3.3	JSP 317	Class II tanks shall be marked ‘Flammable Liquid, No Smoking, No Naked Lights’.
7.3.4	JSP 317	Washing & changing facilities are to be provided for personnel at the place of work. In addition, the following items must also be provided: / Barrier Cream and After Work Cream. / Eyewash (In Date). / Emergency First Aid Kit.
7.3.5	JSP 317	Appropriate Personal Protective Equipment (PPE) and Respiratory Protective Equipment (RPE) is provided and used by all operators.
7.3.6	JSP 317	The quantity and location of all fire fighting equipment, which is determined by the Unit Fire Officer, must reflect what is stated in the Fire Safety Risk Assessment (FSRA).
7.3.7	JSP 317	An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan					FGSR Note: Example Fire Plan provided on JSP 317 website.
7.3.8	JSP 317	Fire Safety Notices & Fire Action Notices must be displayed in order to comply with the Health and Safety (Safety Signs and Signals) Regulations 1996. Locations and quantities should relate to the local risks and be the result of a risk assessment.
7.3.9	JSP 317	Smoking or Smoking materials are not permitted in the hazardous area. Personnel are to deposit any smoking materials in a safe designated contraband area before entering a hazardous zone or likely hazardous area.
7.3.10	JSP 317	Combustible material such as vegetation, litter or rubbish should not be allowed to accumulate in the bund as this will increase the risk of fire.
7.3.11	JSP 317	Grass and Vegetation is to be cut back to a minimum of 15m. Isolated deciduous trees are permitted but conifers must be removed. Grass cutting and removal of vegetation must be carried out iaw the MoD Safety Rules and Procedures for Work on Petroleum installations.

7.4 ENVIRONMENTAL PROTECTION					GRADING
					G					R			N/A				Remarks
Ref
7.4.1	JSP 317	Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
7.4.2	JSP 317	A Pollution Control Point (PCP) is to be established at the installation. The PCP must be clearly identifiable, stocked appropriately and be maintained on a regular basis.
7.4.3	JSP 317	The unit must hold and maintain a local Spillage Register. All spillages are to be recorded and the forwarded to the Pollution Control Officer (PCO), who will collate the establishments, combined spill data.
7.4.4	Example USRP	Spillage Immediate Action Posters are to be prominently displayed at all Pollution Control Points and locations were F&L is stored.

7.5 OPERATING PROCEDURES					GRADING
					G					R					N/A					Remarks
Note: Operating procedures will be assessed on both documentary evidence and a set of verbal responses to the auditor.
AVIATION RECEIPT PROCEDURES
Ref
7.5.1	JSP 317			Aviation Fuel. All materials in contact with aviation fuel are to be MoD approved by both the relevant Fuels Quality Assurance section and the Engineering Authority to ensure that the fuel does not react with the material and vice versa.
7.5.2	JSP 317			What grades of fuel are receipted into the installation and by what method? If F35 is receipted and blended on site answer the relevant blending questions. View the receipt point noting the general condition and cleanliness of the area, the correct fitment of blanking caps and the location of spill and fire equipment.					F18, F34, F35, F44 / Pipeline or BFCV
7.5.3	JSP 317			Before any product is transferred into storage the following actions must be taken / All storage tanks to be used must be suitable for the product and if empty, certified clean. If they contain product it must be of the same grade, free from contamination and within specification and retest date / All filters, connections and associated pipe work must be checked to ensure cleanliness, correct connection and operation. All hatches are to be secured to avoid the ingress of water and other contaminants. / There is sufficient ullage within the storage tank to accept the delivered volume.
7.5.4	JSP 317			When new deliveries of fuel are receipted into storage, the bulk tank contents shall be allowed to settle for a minimum of 2 hrs before any fuel is issued, providing the fuel is filtered into storage. If fuel is filtered into and out of storage i.e a BFCV and Installations filtration systems; in this instance no settling period is required.
7.5.5	JSP 317			A sample must be taken at time of receipt.
7.5.6	JSP 317			Ascertain which tests are being conducted. As a minimum these should be: / Appearance / Density / Conductivity (Not F-44) / FSII (Not F-35) / Test for free water / Results for these tests should be compared to those of the release certificate of the fuel being delivered. / Are records being kept of test data? If so where are these held and how are they logged?
7.5.7	JSP 317			What equipment is held to accomplish the testing conducted at 4.3.6.5? / As a minimum these should be; / 5 Litre Glass Sample Jar NSN 6630-99-224-1105 and Carrier / A suitable Hydrometer for the product being delivered, test jar and thermometer (Check calibration status of the hydrometer and thermometer) OR a handheld densitometer (Check calibration of the densitometer) / Conductivity Meter (Check calibration) / For receipts of F-34 and F-44 then a FSII refractometer is required / In date Shell Water Detection Capsules / Can the operator demonstrate how to use the equipment? / Is the equipment stored in good order, i.e. clean/tidy order, thermometers in an upright position etc?
7.5.8	SOP*			If F-35 is receipted, is it to be delivered to aircraft as F-35 or is blending required to convert it to F-34? If F-35 is to be blended when and where does this occur (State in remarks column): / Between receipt point and storage / Between storage and intermediate storage / Directly into the refuelling vehicle / Directly into the aircraft					*Reference TBC
7.5.9	SOP*			Has the blending apparatus been calibrated?					*Reference TBC
7.5.10	JSP 317			Has the installation operator received sufficient training to enable him to use the blending apparatus and is there a mechanism for checking that the correct level of additives is being blended?					Confirm Army Air Corps Training.
7.5.11	JSP 317			Is the blending additive stored in a suitable location and segregated from other products?

AVIATION STORAGE PROCEDURES
Ref					G					R		N/A				Remarks
7.5.12	JSP 317			The storage media should be appropriate for the product being stored and be in a satisfactory condition. This includes the condition of the tank, appropriate marking of the tank. All blanking caps are to be in place when not in use.
7.5.13	JSP 317			What equipment is held to accomplish the testing of bulk stock? / As a minimum these should be; / Any Level Bottom Sampler (ALBTMS) / 5 Litre Glass Sample Jar NSN 6630-99-224-1105 and Carrier / A suitable Hydrometer for the product, test jar and thermometer (Check calibration status of the hydrometer and thermometer) OR a handheld densitometer (Check calibration of the densitometer) / Conductivity Meter (Check calibration) / For receipts of F-34 and F-44 then a FSII refractometer is required / In date Shell Water Detection Capsules / Ask the operator to demonstrate/talk through how to use the equipment / Is the equipment stored in good order, i.e. clean/tidy order, thermometers in an upright position etc.
7.5.14	JSP 317			Control boards are to be maintained in F&L Sections to ensure that information regarding the state of each bulk aviation fuel storage tank is readily available. The following information as a minimum should be recorded: / Tank number. / Grade of fuel. / Tank capacity. / Stock. / Ullage. / Tanks into which bulk receipts are to be accepted. / Tanks from which issues are to be made. / Date of next tank clean. / Date of last update. / Density of fuel @ 15°c (density reading taken from BFI after a receipt).
7.5.15	DLF			Frequency of Dips / Daily. All In-use bulk fuel storage tanks and Bulk Fuel Carrying Vehicles (BFCV) are to be dipped daily. This can be carried out by ATG (if accurate to +/- 1mm and +/- 0.5oC) or manually and, whenever possible before issues of the day. / Weekly. The dip, water check and temperature measurement (temperature is not required for BFCVs) of all bulk storage tanks and BFCVs, including those where no fuel movement has taken place, is to be carried out once a week under the supervision of an authorised officer, normally Fridays. / Last Working Day of the Month. Dips are to be carried out on the last working day of the month under the supervision of an authorised officer (OC Supply at RAF Units).
7.5.16	JSP 317			Are frequent water drains being conducted? / What is the frequency of tank dips and are records maintained. / Water drains shall be recorded (date and volume collected) / When conducted has anything unusual been noted e.g. a smell of rotten eggs is indicative of Micro Biological Contamination , large volumes of water would indicate more frequent drains required / Records shall be kept of all dips that should be conducted weekly and after all deliveries.
7.5.17	JSP 317			Elimination of Water from Storage Tanks 1/4. / The presence of water in storage tanks can give rise to microbiological contamination, and the leaching out of additives. Every effort is to be made to eliminate water in storage tanks. To ensure that water in fuel tanks is kept to a minimum, the following procedures are to be applied: / a. Tanks fitted with automatic water detection and an integrated water removal systems, or automatic tank gauges (ATG), compliant with STANAG 7011, are to be checked for water once a month.
7.5.18	JSP 317			Elimination of Water from Storage Tanks 2/4. / b. Tanks fitted with an ATG, compliant with STANAG 7011, are to be checked for water once a week. Where the tank has not issued or received fuel during the previous week, or where local conditions preclude weekly water checks from being conducted, the frequency of checks may be extended to a period not exceeding one month.
7.5.19	JSP 317			Elimination of Water from Storage Tanks 3/4. / c. Tanks which are not fitted with an ATG are to be checked for water whenever the tank contents are dipped. If water is detected in a tank that is not fitted with an automatic water detection system which incorporates an integrated water removal system, a works service request is to be raised for its immediate removal. The results of all water checks are to be recorded and stock adjustments made in accordance with JSP 886.
7.5.20	JSP 317			Elimination of Water from Storage Tanks 4/4. / d. Filter Water Separators (FWS), fuel monitors and low points in the pipework, where fitted with drain points and used for the issue of fuel in the preceding 24 hrs, are to be checked for water prior to use. Any water found is to be drained off prior to use.

AVIATION FILTRATION PROCEDURES

7.5.21	JSP 317			Only Filter Water Separators (FWS) shall be in use, particularly where the fuel handled is F-34/F-44. If a fuel filter Monitor vessel is installed in a system that handles fuels containing FSII, they should be appropriately marked to identify that NO elements are installed. / There may be incidental occurrence where fuel filter monitors are still in use. In such cases they shall ONLY be used for filtering F-35 aviation fuel and every precaution SHALL have been taken to ensure segregation from fuels that do contain FSII (even trace amounts). / Check the external appearance of the vessel. Ensure that the Data Plate is in place on the vessel recording information on its design and its maximum rated flow. / Are the elements installed all: / From the same manufacturer / Of the same type / Within date (3 year max life from date of installation) / The total rated flow of the elements is greater than the rated flow of the vessel / Pressure Differential gauge is calibrated and functioning. / Certificate is available / Gauge is clearly identified / Is the pressure differential (PD) recorded for the vessel when in use / The maximum PD for a FWS is 15 psi, at which point the elements should be changed / The maximum PD should be recorded weekly / The maximum PD should be recorded at, or adjusted to the maximum rated flow
7.5.22	JSP 317			Maintain accurate monitoring of differential pressure across the filters as this is the only guide to their condition. If the pressure rises beyond the acceptable limits (15 psi) the cartridges are to be replaced. / *Note: PD reduction ratio taken from the manufacturers accompanying literature. Record readings in RAF F6816 (FWS & FM Log)					*PD reduction: / 90% - / 80% - / 70% - / 60% - / 50% -
7.5.23	JSP 317			Note: Coalescer elements should be replaced when the PD reaches 15 psi at their maximum rated flow. If however, the vessel is operated at a lower flow rate, the maximum PD of 15 psi will be reduced.* / Are water drains (of the FWS sump) being conducted and recorded? / When conducted has anything unusual been noted e.g. a smell of rotten eggs is indicative of Micro Biological Contamination? / If the system permits direct delivery to aircraft without passing through a further FWS, has a valid Millipore test been conducted within the last three months that provided a satisfactory result.

AVIATION BULK ISSUES
Ref					G					R		N/A				Remarks
7.5.24	JSP 317			Turnover of Stocks / Stocks are always to be issued on the principle of using oldest stock first. The age of stock is to be assessed by the length of time it has been in storage in the installation. Where an installation has two or more tanks, the tanks are to be filled and emptied in rotation.
7.5.25	JSP 317			Before issue all hoses and couplings are to be visually checked for signs of general deterioration. It is essential that the coupling is kept scrupulously clean and the protective cap kept in position when not in use. When in use hoses and couplings are to be inspected periodically, as outlined below. The inspections are to be conducted on at least a quarterly basis, although more frequent checks may be required depending on local conditions. Standing Operating Procedures are to outline the frequency and method of recording such checks.
7.5.26	JSP 317			BFCV and BFI Daily Checks / When BFCVs are being loaded or unloaded the following actions are to be taken: / a. Immediately on entering a civilian or MoD installation inclusive of Field Bulk Fuel Installations (FBFI) the driver is to report to the site control point/office for the relevant instructions in: / (1) Emergency Procedures. / (2) Loading Operations. / (3) Traffic Control Systems. / b. It is the BFCV drivers responsibility to carry out the following actions: / (1) Ensure the vehicle is positioned so it is able to exit the installation without reversing or carrying out a complicated manoeuvre in the event of an emergency. / (2) Assist the installation competent person in completing paperwork. / (3) Earth and Bond the vehicle to the installation. / (4) Ensure that the vehicle master switch is off once the vehicle is parked in the relevant position (unless required to drive pump). / (5) Vehicle fire extinguishers are to be placed 5 m upwind and the relevant hazard warning signs are displayed upon the approach to the vehicle location. / (6) Man lids are opened. / c. Before any operations commence the driver and installation competent person are to confirm the Quality, Quantity and Grade (QQG) of the product being loaded/unloaded in both the BFCV and the receiving / issuing tank. / d. All operations are to be in constant visual supervision of a certified competent person. Pump sets and delivery hoses are not to be left unattended during operations. / e. It is important that any temporary bonding connections that are made should not be liable to accidental damage. / f. Before receipt from a civilian tanker takes place, all seals on the manifold are to be inspected to ensure that the load has not been tampered with. / g. Where fuel is being transferred between two BFCVs, they are to be bonded together. Where applicable, vehicles are to be earthed. / h. BFCV dedicated solely for the storage, issue and receipt of AVGAS are not required to be fitted with a FWS. The need for a mesh screen filter remains extant.
7.5.27	JSP 317			Filter Water Separators (FWS), fuel monitors and low points in the pipe work which are fitted with drain points and have been used for the issue of fuel in the preceding 24 hrs are to be checked for water prior to use. Any water found is to be drained off prior to operation of the equipment.

OPERATION OF AVIATION BULK FUEL CARRYING & HYDRANT REFUELLING VEHICLES
Ref					G				R			N/A			Remarks
7.5.28	JSP 317			Are the following first parade/pre delivery checks being conducted on aviation fuel: / Appearance / Density / Water Detection / At the following intervals: / The start of each day / After 180 minutes (3 hours) if no aircraft have been refuelled following the start of day check / After bulking of the BFCV (a minimum of 10 minutes shall be allowed for the fuel to settle post loading before a sample is taken) / At change of shift/driver / Every 10 days if the vehicle is currently out of use / A sample shall be drawn from the tank drain and examined for; / Appearance (Clear and Bright and free from particulate matter) / Test for free water (Shell Water Detection test)
7.5.29	JSP 317			Issue of Aviation Fuel from BFCVs / It is recommended that all bulk fuel carrying vehicles be kept as full as is practical at all times and carrier tanks should be filled to 90% of their capacity at the end of the operating period / day to minimise the amount of water formed thereby reducing the risk of microbiological contamination and also depletion of the Fuel System Icing Inhibitor (FSII) in the fuel. / Samples are to be taken from the sump of the carrier tank. Contamination tests are to be carried out: / a. Each time the vehicle receives fuel from any source, and after a minimum settling time of 10 minutes. / b. Where a fuelling vehicle has been out of use for a period of 10 days the contamination test is carried out on the 11th day and is repeated at ten day intervals during the period for which the vehicle is not in use.
7.5.30	JSP 317			Only Filter Water Separators (FWS) shall be in use, particularly where the fuel handled is F-34/F-44. If a fuel filter Monitor vessel is installed in a system that handles fuels containing FSII, they should be appropriately marked to identify that NO elements are installed. / There may be incidental occurrence where fuel filter monitors are still in use. In such cases they shall ONLY be used for filtering F-35 aviation fuel and every precaution SHALL have been taken to ensure segregation from fuels that do contain FSII (even trace amounts). / Check the external appearance of the vessel. Ensure that the Data Plate is in place on the vessel recording information on its design and its maximum rated flow. / Are the elements installed all: / From the same manufacturer / Of the same type / Within date (3 year max life from date of installation) / The total rated flow of the elements is greater than the rated flow of the vessel / Pressure Differential gauge is calibrated and functioning. / Certificate is available / Gauge is clearly identified / Is the pressure differential (PD) recorded for the vessel when in use / The maximum PD for a FWS is 15 psi, at which point the elements should be changed / The maximum PD should be recorded weekly / The maximum PD should be recorded at, or adjusted to the maximum rated flow
7.5.31	JSP 317			Maintain accurate monitoring of differential pressure across the filters as this is the only guide to their condition. If the pressure rises beyond the acceptable limits (15 psi) the cartridges are to be replaced. / *Note: PD reduction ratio taken from the manufacturers accompanying literature. Record readings on MoD F7765.					*PD reduction ratio: / 90% - / 80% - / 70% - / 60% - / 50% -
7.5.32	JSP 317			Note: Coalescer elements should be replaced when the PD reaches 15 psi at their maximum rated flow. If however, the vessel is operated at a lower flow rate, the maximum PD of 15 psi will be reduced.* / Are water drains (of the FWS sump) being conducted and recorded / When conducted has anything unusual been noted e.g. a smell of rotten eggs is indicative of Micro Biological Contamination. / If the system permits direct delivery to aircraft without passing through a further FWS, has a valid Millipore test been conducted within the last three months that provided a satisfactory result.

8.	JOFS

STORAGE TANKS

Tank No.	Serial No.	Date		Capacity / (m³)	Product	IER Dates		Remarks
		Manufactured	Into Service			Last Insp	Next due

PUMPS

Pump / No.	Serial No.	Model/Type/ / Rate	Date		Product	IER date		Remarks
			Manufactured	Into Service		Last Insp	Next due

BUND LINERS

Bund / Location	Serial No.	Date		Product	IER Dates		Remarks
		Manufactured	Into Service		Last Insp	Next due

TACTICAL FUEL HANDLING EQUIPMENT (TFHE) / JOFS
Note: All Deployed Bulk Fuel Installations (DBFIs) regardless of size are to meet the requirements of this section. The definition of a DBFI is referenced to Military Engineering Volume XII. Where the rapid nature of deployment and recovery during operations within a Military Works Area preclude a full planning cycle, it may not be pertinent to consider all stated aspects herein, but for all instances of training and as soon as possible on operations, all aspects of the FSAA (in respect of DBFIs) should be considered. Users of DBFIs should not limit their references to JSP 309 & 317 and should demonstrate a thorough understanding and application of those other regulatory/ legislative instruments which are provided for various products or activities undertaken, or concluded within the confines of a DBFI (Container filling, aviation refuelling, BFCV operations, packed stock storage etc) / Note: Units deploying JOFS/TFHE are to self assess using the Fuel Safety Assurance Assessment (FSAA). One copy is to be held at unit level for up to three years and a second copy shall be provided to their relevant Fuels RO or Command. SOPs and TOPs may not be referenced and as a result these observations will not be regulated by the FGSR. In this instance the reference column will state ‘SOP’ or ‘TOP’.

8.1 INSTALLATION DOCUMENTATION			GRADING
			G			R		N/A			Remarks
Ref
8.1	TOP	Person in charge (PinC) has been nominated?
8.1.1	JSP 317	Recce Report has been produced and is available.
8.1.2	JSP 317	Earth Testing and Electrical Continuity checks completed and recorded?
8.1.3	JSP 317	Pneumatic Leak Testing completed and recorded?
8.1.4	JSP 317	Hydraulic Leak Testing completed and recorded?
8.1.5	JSP 317	All documents and plans completed as per the Master Check List.
8.1.6	JSP 317	Following construction, the Operating Authority should receive a formal handover from RE personnel. A completed handover certificate should be available at the installation.
8.1.7	JSP 317	Safe System of Work is adhered to?
8.1.8	SOP	Issue vouchers for stores and lists for all equipment on site.
8.1.9		Plant Docs and tank record books available.
8.1.10		Instructions on operations of any unfamiliar components.
8.1.11		Drawing recording site layout and valve setting chart.
8.1.12	TOP	Permitting system in place and controlled by AP (Pet)?

8.2 OPERATION & FUNCTION				GRADING
				G			R		N/A		Remarks
Ref*
8.2.1	JSP 317	The installation has been designed, constructed and approved iaw the requirements of JSP 317 and Mil Eng Vol XII.
8.2.2	JSP 317	Personnel responsible for the siting of DBFI’s are to consider the following: / Siting boards should take place when possible. Where this is not possible, a recce is to produce a Formal Recce Report in its place. / Should allow for the dispersion of vapours / The release of contaminated water etc (bund water etc is to be treated as contaminated waste) / Vehicular access from MSR’s / Dispersion of stocks / Separation and safety distances from other areas such as: / Ammunition >50 m (ATO to advise) / Antenna Farms - Advice from Technical Authority / Accommodation & sleeping areas >45m (Fire Advisor (FA) to advise) / Occupied buildings and possible sources of ignition - Advice from FA: / Class I & II products min >15m / Class III product min >10m / Flight-paths - Advice from SATCO
8.2.3	JSP 317	Camouflage, Concealment and Deception (CCD) If camouflage nets are used they must be a minimum of 1m above bund walls to allow for dispersion of vapour.
8.2.4	JSP 317	Concealment of BFCV’s The following guidance shall be followed when Camouflaging BFCVs not fitted with the Mobile Camouflage System: / a. Hessian or any other combustible materials shall not to be used. / b. Camouflage netting and Urban Cam of any type is not to be draped directly onto any part of the vehicle. / c. The hide should be constructed as to allow the BFCV to be driven in and out without fouling the camouflage netting. / d. The Camouflage net should be high enough to allow the driver/operator to dip the tank without difficulty. / e. Camouflage nets must be fire-retardant. / f. Camouflage nets contaminated with fuels shall not be used. Camouflage nets contaminated with fuels should be handled with care due to the risk of spontaneous combustion.
8.2.5	Mil Eng XII / Para 1724	FWS located as close to dispense points as possible.
8.2.6	JSP 317	Bunds constructed in accordance with Mil Eng Vol XII and making provision for: / Bund floor free of sharp objects and max slope of 1:60 towards the dispensing end. / Bund floor provided with sump. / Bund wall to be continuous and capable of containing 110% of the largest tank they contain. / No more than 2 x 136m³ TFC’s per bund / Where possible bunds are to be separated from one another / Bunds shall be constructed of non-flammable material
8.2.7	JSP 317	Traffic Circuits must be adequate to allow the passage of delivery/receipt vehicles as well as allowing for unhindered passage of fire fighting vehicles. Access and egress to the site must be controlled and where necessary, physical protection measures may be required to protect exposed pipework/equipment from vehicle damage.

8.3 FIRE, HEALTH & SAFETY				GRADING
				G			R		N/A		Remarks
Ref
8.3.1	JSP 317	Washing & changing facilities are to be provided for personnel at the place of work. In addition, the following items must also be provided: / Barrier Cream and After Work Cream. / Eyewash (In Date). / Emergency First Aid Kit.
8.3.2	JSP 317	Appropriate Personal Protective Equipment (PPE) and Respiratory Protective Equipment (RPE) is provided and used by all operators.
8.3.3	JSP 317	Smoking or Smoking materials are not permitted in the hazardous area. Personnel are to deposit any smoking materials in a safe designated contraband area before entering a hazardous zone or likely hazardous area.
8.3.4	JSP 317	Following consultation with the Defence Fire Service (DFS), Landowners and possibly the local Fire Brigade the appropriate scale of Fire Fighting Equipment is provided at the facility and is positioned to afford the maximum protection for the entire installation.
8.3.5	JSP 317	The following Hazard Warning Signs stating ‘Petroleum Spirit, Highly Flammable, No Smoking, No Naked Lights’ must be displayed on all approaches to the facility in local language and English:
8.3.6	JSP 317	All sites boundaries must display the correct ‘Ex’ warning sign.

8.4 ENVIRONMENTAL PROTECTION				GRADING
				G			R		N/A		Remarks
Ref
8.4.1	JSP 317	Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
8.4.2	JSP 317	Sufficient Pollution Control Points (PCP) are established at the installation. The PCPs must be clearly identifiable, stocked appropriately and be maintained on a regular basis.
8.4.3	JSP 317	Bund Water. All water which accumulates in the bund is to be classed as contaminated waste and consideration should be given to placement of interceptors if required and waste water removal by contractor.

8.5 STANDARD OPERATING PROCEDURES				GRADING
				G			R		N/A		Remarks
Ref
8.5.1	SOP	Issue vouchers for stores and lists available for all equipment on site.
8.5.2	SOP	Fire Practice conducted and recorded, prior to in-load of product?
8.5.3	SOP	Rehearsal of the USRP conducted and recorded prior to in-load of product?
8.5.4	SOP	No unauthorised personnel. Where personnel require access but are not in receipt of a COC for the installation, are arrangements in place to provide adequate and constant supervision?
8.5.5	SOP	Training delivered and competence assessed and recorded for all operations and procedures conducted on the installation?
8.5.6	SOP	Safety Brief for visitors (including all drivers)?
8.5.7	SOP	Question visiting drivers on emergency procedures.
8.5.8	SOP	Provision of valves to permit commissioning, decommissioning and repair of the installation?
8.5.9	SOP	Bunding or drip trays for all pumps, manifolds, FWS and sand and stone traps?
8.5.10	SOP	Adequate ullage provided to accept emergency transfer from tanks containing products of the same grade?
8.5.11	SOP	Tanks not to be filled above 100% of their max working capacity?
8.5.12	SOP	Water drained off daily. Use of water finding paste?
8.5.13	SOP	Daily visual inspections of all TFC and pipelines?

9.	BULK FUEL CARRYING VEHICLE (BFCV) STORAGE PARK

Interceptor Capacity ___________________m³

9.1 OPERATION & FUNCTION			GRADING
			G	R	N/A	Remarks
Ref
9.1.1	JSP 317	The hard standing is to be of sufficient size to accommodate all establishment BFCVs. In addition there must also be sufficient area for manoeuvring and an additional area dedicated for transiting or visiting unit BFCVs. Calculations for determining the area should be 2.25 x the floor plan area of each vehicle e.g 9 Tonne MM Unit Support Tanker (UST): 2.55m x 9.16m x 2.25 = 52.56 m².
9.1.2	JSP 317	The hard standing surface must be constructed of concrete or another material that is impervious to hydrocarbons.
9.1.3	JSP 317	In all instances there is to be a safety distance around the hard standing, extending outwards 10m in all directions. No facilities, vehicle parking areas or buildings, including control rooms, are permitted within this safety distance.
9.1.4	JSP 317	A 45m Safety distance applies to living accommodation & public highways. The Siting Board can give dispensation to reduce the distance from a public highway to a min of 10m, however the distance from living accommodation must not be reduced.
9.1.5	JSP 317	Drainage The ground must be sloped towards catchment drain/drains.
9.1.6	JSP 317	If the interceptor capacity is less than the largest, single, vehicle compartment, answer the following Mitigation question below.				KPI
9.1.7	JSP 317	OWI Mitigation Pollution ERA: / If the Interceptor has been identified as below the required capacity, has a suitable Pollution ERA been carried out, recorded, and is it annually reviewed to mitigate the increased risk? / If the Pollution ERA mitigates the insufficient capacity by demonstrating a work around solution, subsequent assessments can be assessed as Green				.
9.1.8	JSP 317	OWI Maintenance: These assets are maintained under Project Aquatrine by Aquatrine Service Providers. As a minimum, every 6 months or iaw manufacturers’ instructions, OWIs should be physically inspected to: / Ensure the Integrity of OWI / Identify the quantity of any accumulated F&L and silt. / Confirm that all electrical equipment is functioning correctly i.e Alarms. / Inspect the Condition of any coalescing devices and replace if necessary. / There must be evidence to clearly demonstrate that all the above points have been completed for this serial to be graded compliant. / The last inspection of the Interceptor was conducted by ___________ on ___________. If this date exceeds 6 months or the date of the last inspection cannot be ascertained award a ‘Red’ grade for this question.				FGSR Note: The Aquatrine contract only includes mainland UK units. In all other instances host nation standards will apply. / KPI
9.1.9	JSP 317	Illumination. Overhead lighting is to be a minimum 20 Lux iaw JSP 315.
9.1.10	JSP 317	The BFCV Park is to be surrounded and secured by a 1.8m / High chain link fence. The perimeter fence should be positioned no less than 10m from the edge of the BFCV hard standing if it forms part of the camp perimeter and no less than 2m if not.
9.1.11	JSP 317	Entrance/exit gates must open outwards and must not be self-locking. Securing mechanisms must be operable utilizing a single action device, without resorting to the use of a key. Gates must be capable of being bolted or held open.
9.1.12	JSP 317	Emergency shower. The removal or changing of clothing inside the Hazardous Areas is prohibited. In order to enable contaminated clothing to be quickly and safely removed avoiding ignition from static electricity, a deluge shower is to be installed. Showers are to be sited at the entrance of the park, however where this is not possible, alternative arrangements are to be made in conjunction with the production of a risk assessment.				Award a red grade for this serial if no RA is produced.
9.1.13	JSP 317	Traffic Flow. Under normal circumstances a one-way traffic system incorporating an exit and access gate is to be approved, based upon a risk assessment and the number of BFCVs operated. Where this requirement is deemed unnecessary it may still be necessary to impose restrictions on the outcome of a risk assessment such as: / If the distance to travel to exit the park exceeds 24m a personnel emergency exit should to be included in the design. / If only one exit is used the width of the park entrance and approach road may need to be increased to allow two-way traffic flow. / Appropriate traffic flow indication markings to be incorporated within and around the park. / Design must allow parked vehicles to be driven forward to the nearest/safest exit without the need to manoeuvre/reverse, in the event of an emergency.
9.1.14	JSP 317	Earthing/Bonding. Bulk Transfer areas are to be equipped with fixed earth points. Fixed earth points are not required outside of this area. BFCVs stored/parked in the facility are to utilise fitted CES items.
9.1.15	JSP 317	Transfers must only to take place in a designated area of the BFCV Park. The transfer area is to be marked and a safety distance of 15m is to be established around the two BFCVs from any other vehicle.
9.1.16	JSP 317	Safety Distances BFCV Parking. Area provided in accordance with JSP 317- 2.25m for each vehicle, 1m between UBRE/UST & 2m between Support Tankers (all variants). 3m between groups of 9 UBRE & 5m between groups of 9 Support Tankers

9.2 FIRE, HEALTH & SAFETY			GRADING
			G	R	N/A	Remarks
Ref
9.2.1	JSP 317	Communications. Does the unit have an effective means of both raising the alarm & giving warning in case of fire?
9.2.2	JSP 317	The following Hazard Warning Sign stating ‘Petroleum Mixture, Highly Flammable, No Smoking/Naked flames, No mobile phones, No parking’ is to be displayed on all approaches to the facility in the local language and English:
9.2.3	JSP 317	Hazardous Area. The hazardous area extends to 10m beyond the physical boundaries of the BFCV Park. The following items/activities are not permitted within this distance: / Smoking or naked flames. / Studded footwear. / Tracked vehicles. / Mobile or portable phones unless ATEX certified. / Consumption of food. / The removal of contaminated clothing. / Hearing Aids, unless they have been certified as intrinsically safe. If they are certified the user must be briefed not to change or expose the batteries in the hazardous area.
9.2.4	JSP 317	Security/Access. Access to the facility is to be restricted to authorised, trained, duty personnel. When unoccupied BFCV Park gates are to be locked and keys must be held in safe custody. Access to the keys should be restricted to authorised personnel only. Any visitors who have not received a mandatory safety brief before entering the facility must be supervised by a competent person at all times.
9.2.5	JSP 317	Contraband. There must be a system in place to deposit contraband and any smoking materials prior to entering the hazardous area.
9.2.6	JSP 317	Vehicle Repairs. Hot or electrical BFCV repairs are not permitted within the BFCV Park.
9.2.7	JSP 317	Contaminated Clothing. Clothing contaminated with F&L products should be removed as soon as possible however before removing; operators should ensure they have taken all necessary precautions to guard against static discharge. Clothing contaminated with Class I or Class II products should only be removed after saturating with water using the Drench Shower.
9.2.8	JSP 317	Ammunition. The storage or carriage of ammunition is prohibited inside the hazardous area.
9.2.9	JSP 317	An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan
9.2.10	JSP 317	Fire Fighting Apparatus. Min 2 x 90 litre for first 12 vehicles and one for each additional 12 or part thereof. Extinguishers are to be sited not less than 15m from any BFCV in an easily accessible position.
9.2.11	JSP 317	Fire Safety Notices & Fire Action Notices must be displayed in order to comply with the Health and Safety (Safety Signs and Signals) Regulations 1996. Locations and quantities should relate to the local risks and be the result of a risk assessment.
9.2.12	JSP 317	First Aid & Eye Wash. Provisions for emergency first aid treatment are to be made, in conjunction with appropriately trained and qualified personnel. First Aid points (including eye wash facilities) are to be established and locations are to be clearly identified i.e. signposted.
9.2.13	JSP 317	Toilets, washing and changing facility. To be provided within 50m of BFCV Park entrance. Adequate supplies of pre-work barrier and after work cream to be provided at this facility.
9.2.14	JSP 317	Personal Protective Equipment (PPE). HoE is to ensure employees are informed, instructed and trained in the following areas: / The risks PPE is designed to protect against and limitations. / The correct use of PPE and its purpose. / Actions required by personnel to avoid exposure to hazards.
9.2.15	JSP 317	PPE HoE is to provide employees with adequate PPE and must take all reasonable steps to ensure it is being used correctly and is inspected iaw the requirements JSP 375.
9.2.16	JSP 317	PPE HoE must provide suitable storage for the PPE to : / Protect it from the hazard for which it was provided and any other hazard that may damage it or cause it to be hazardous. / Ensure it is stored in a clean, hygienic location.
9.2.17	JSP 317	PPE Employees are responsible for ensuring that they: / Make full and proper use of their PPE. / Make sure it is stored in the designated area when not in use. / Report any damaged PPE to their CoC immediately.
9.2.18	JSP 317	Emergency Action Point (EAP). An EAP is to be established as close to the park entrance as possible, but at least 15m from the closest parked BFCV. The list is not exhaustive but as a minimum the EAP should include the following: / Hazard Warning Signs. / Pollution Control Point. / Fire Extinguisher / Notice Board, suitably weather proofed, displaying the following: / Site specific Comprehensive Fire Plan. / Pollution Control Plan. / DSEAR RA. / COSHH RAs & relevant Safety Data Sheets.
9.2.19	JSP 317	Instructions in Writing. When vehicles contain product within the storage tank or they are classed as nominally empty, Instructions in Writing must be displayed at all times. Where vehicles have been gas freed, Instructions in Writing must either be removed or placed in a securely closed container marked “Not relating to dangerous goods carried”.
9.2.20	JSP 317	Instructions in Writing (cont). Where it is necessary to de-couple articulated BFCVs, the Instructions in Writing must be removed from the vehicle cab and be securely attached to the trailer unit in a weather-proof enclosure. Kemlar plates attached to the front of the trailer to assist emergency services.

9.3 ENVIRONMENTAL PROTECTION			GRADING
			G	R	N/A	Remarks
Ref
9.3.1	JSP 317	User units have a responsibility to ensure that the Aquatrine Service Provider (ASP) maintains, services and routinely inspects/cleans the facilities interceptor. The unit Site Estate Team Leader (SETL) is usually the Aquatrine Liaison Representative (ALR) and they should be contacted in the first instance if the unit feel the ASP are failing to fulfil this requirement.
9.3.2	JSP 317	Units are to contact their Regional Prime Contractor (RPC), DIO and the SETL if a significant spillage occurs at the facility or when they suspect that the interceptor is full and requires emptying.
9.3.3	JSP 317	Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
9.3.4	JSP 317	A Pollution Control Plan is to be provided for the BFCV Park iaw JSP 317, Part 5, Chap 2. A copy of the plan is to be included in the Unit Spillage Response Plan (USRP).
9.3.5	JSP 317	Pollution Control Point (PCP). 1x PCP is to be provided for the first 8 x BFCVs and one additional PCP for the next 8 x BFCVs of parts thereof. Each PCP should be marker ‘POLLUTION CONTROL POINT’ and should contain the following: / Contents, instruction leaflet and Pollution Control Plan. / 100 Ltrs of loose absorbent. / 20 Flat pads. / 4 Oil seal/tube pads. / 2 x Stiff brooms. / 2 x Shovels. / 2 x large drip trays. / 6 x disposable polythene sacks and ties.				BFCVs PCPs / 8 1 / 9-16 2 / 17-24 3 / 25-32 4
9.3.6	JSP 317	Spillage Immediate Action Posters are to be prominently displayed at all Pollution Control Points and locations were F&L is stored.				FGSR Note: Para 5 of example USRP.

9.4 OPERATING PROCEDURES			GRADING
			G	R	N/A	Remarks
Ref
9.4.1	JSP 317	Vegetation within the hazardous area is to be maintained and should not present a fire hazard. Isolated deciduous trees may be left in situ, providing overhanging foliage is cut back. Coniferous trees are not permitted within the hazardous area.
9.4.2	JSP 317	Housekeeping. Waste, contaminated pollution control sorbents and any other material used for cleaning purposes must be removed from the hazardous area immediately after use.
9.4.3	JSP 317	Skips/Bins. Skips, bins or other containers, used for the storage of contaminated materials, are not to be sited within the hazardous area.
9.4.4	JSP 317	Parking. Vehicles must be guided into parking bays and must not overhang the edge of the hard standing.

10.	UNINSTALLED ENGINE TEST FACILITY (UETF)

10.1 MAINTENANCE					GRADING
					G	R		N/A	Remarks
Ref
10.1.1	DIO Practitioner Guide / PG 06/12		Inspection of the Fuel Infrastructure and Flammable Goods Facilities (Previously known as Task 249) : / An Inspection of the Fuel Infrastructure and Flammable Goods Facilities was carried out on _____________. A Certificate of Fitness for Continued Use was Issued for a period of _____ months . If the facility was considered ‘Not Fit For Continued Use’ or the unit were given a specified timeframe to rectify observations in the ‘Table of Defects’, which has lapsed without rectification, grade this question as Red and answer the following ‘Action Plan’ question. / *If this question is graded Red, answer the following Action Plan question.						FGSR Note: / Regulation / KPI
10.1.2	As above.		Inspection of the Fuel Infrastructure and Flammable Goods Facilities Action Plan (If applicable): / An Action Plan has been produced and funding has been allocated to rectify the specific observations detailed in the ‘Table of defects’ which warranted the ‘Not Fit for Continued Use’ grading.						If green, send copy with completed report
10.1.3	DIO Practitioners Guide 05/12		Electrical Systems Test (Annual): / The Installations Electrical System was tested iaw the requirements of PG 05/12 on ____________ and was graded as ‘Satisfactory’. An ‘Unsatisfactory’ grade should be awarded ‘Red’ for this question. / *If this question is graded Red, answer the following Electrical Test Action Plan question.						FGSR Note: / Regulation / KPI
10.1.4	As above.		Electrical Systems Test Action Plan (If applicable): / An Action Plan has been produced and funding has been allocated to rectify the specific observations which resulted in the ‘Unsatisfactory’ Electrical Test grading.						If green, send copy with completed report
10.1.5	JSP 317		Lightning Protection (If applicable) / If the installation is located in an area susceptible to lightning / BS 6651 and BS EN 62305 are to be consulted to determine whether lightning protection is required. If it is required, protection installed at installations constructed prior to 31 Aug 08 is to be maintained iaw the requirements of BS 6651 until such time that the installation is upgraded, after which BS EN 62305 will apply. Lightning protection installed on or after 31 Aug 08 is to be installed and maintained iaw the requirements of BS EN 62305.
10.1.6	DIO PG 06/12 / Annex B		Level 1 Assessment (Underground Single Skinned Steel Tanks (USSST)): / Level 1 Assessments were conducted on __________ and the cumulative scores were______________________________.						A tank is deemed to be a high risk if the cumulative score exceeds +6.
10.1.7	DIO PG 06/12 / Annex B / D&MG 14 / Chap 15.2 / Table 1		Level 2 Testing, Tank Tightness Tests of USSST: / The Installation was constructed in________. The last Level 2 Testing was undertaken on the installations storage tanks on ________. The next Tank Tightness Tests are due on _______________________.						USSST shall undergo Level 2 testing in years 20, 25, 30 and every 2 years thereafter as a minimum and more frequently if the level 1 assessment deems it necessary.

10.2 OPERATION & FUNCTION					GRADING
					G	R	N/A		Remarks
Ref
10.2.1	JSP 317		Does the installation design and layout provide means of escape for employees and means of access for the fire brigade in the event of a fire? Answer Green for ‘Yes’ and Red for ‘No’.
10.2.2	JSP 317		Overhead Power Cables are not permitted to cross the installations Hazardous Area.
10.2.3	JSP 317		Above Ground Storage Tanks- Secondary Containment The bund wall must be capable of retaining 110% of the largest container within the bund or 25% of the aggregate of multiple containers, whichever is greater.
10.2.4	JSP 317		Compliant Integrally Bunded Storage Tank. Defined as ‘An above ground storage tank which has an integral secondary containment system, capable of containing 110% of the primary containers brim-full capacity. If this storage media is employed, an additional bund will not be required however the tank must be sited on an impermeable surface and be isolated from the surface water drainage system.
10.2.5	APEA Design, Con, Mod, Maint & Decom of Filling Stations / Para 11.6		Tank Contents Measurement Method. All tanks or compartments should be provided with a means of ascertaining the quantity of fuel stored. This may be by use of a dipstick or by some means of tank contents gauge. Indicate which method is used in the remarks column.						Manual Dip* / Auto Tank Gauge* / *Delete as applicable
10.2.6	JSP 317		Above Ground Storage Tanks- Secondary Containment The bund wall must: / Be impervious to liquid / Not normally be higher than 1.5m high. / Be fitted with crash protection if susceptible to impact damage e.g adjacent to a vehicle manoeuvring area.
10.2.7	JSP 317		Above Ground Storage Tanks- Secondary Containment. In order to prevent jetting; a phenomenon caused when the primary container fails and F&L is propelled at force beyond the secondary containment, the bund wall is not to be constructed too close to the tank.
10.2.8	JSP 317		Above Ground Storage Tanks - Secondary Containment The bund base and walls must not be penetrated by any valve, pipe or other opening which is used for draining the bund. Where a tank fill or draw off pipe must pass through the bund base or wall, the hole must be carefully sealed with a fire resistant seal to prevent oil escaping.
10.2.9	JSP 317		Above Ground Storage Tanks - Secondary Containment Rainwater which collects in the sump must be removed on a regular basis to ensure the bund capacity is maintained. This water is to be disposed of appropriately to ensure no pollution occurs.
10.2.10	JSP 317		Inspection of Bunds - Bunds should be regularly inspected for signs of damage and checked for water by the operator on a weekly basis.
10.2.11	JSP 317		Above Ground Storage Tanks - Secondary Containment If oil or a mixture of oil and water is found in the bund it must be disposed of in accordance with current Hazardous Waste Regulations.
10.2.12	Oil Storage Regs 3 (3)		Above Ground Storage Tanks- Secondary Containment Valves should be as resistant to unauthorised interference and vandalism as far as is feasibly possible, with lockable or removable hand wheels.
10.2.13	OSR 01 / Reg 3(3)		Above Ground Storage Tank- Secondary Containment s All tank vent pipes, valves, filters, sight gauges and any other ancillary equipment with the exception of the fill pipe, draw off pipe or pump if the fuel has a flashpoint of less than 32ºc, must be positioned within the bund wall.
10.2.14	OSR 01 / Reg 3(3)		Above Ground Storage Tanks Valves should be marked to indicate whether they are open or closed, kept locked when not in use and fitted with a blanking cap or plug.
10.2.15	OSR 01 / Guidance Para 38		Above Ground Storage Tank- The connection point is to be located inside bund wall or be located in a position which allows for containment.
10.2.16	JSP 317		Above Ground Storage Tank- - Sight Glasses The use of sight glasses should be limited to the storage of Class II & III fuel tanks with a maximum capacity of 3500 Ltrs. If sight glasses are fitted they shall: / Be located in the secondary containment. / Be properly supported so that they cannot come loose. / Be fitted with a valve that automatically closes when the sight glass is not in use. / Be fitted with valves which are kept closed when not in use and only opened when taking contents readings.
10.2.17	JSP 317		Above Ground Storage Tank- - Small Tank Minimum Separation Distances. A small tank is considered to be a tank with a diameter of less than 10m. The minimum separation distances from site boundaries, fixed sources of ignition, buildings and process areas for single small tanks are as follows: / Tank Capacity (m³) Separation (m) / Less than or equal to 1 1* / Greater than 1 and less than or equal to 5 4 / Greater than 5 and less than or equal to 33 6 / Greater than 33 and less than or equal to 100 8 / *In this instance the tank must be sited at least 2m from doors, plain glazed windows, other openings or means of escape. In addition they must not be below openings from an upper floor, regardless of vertical distance.
10.2.18	PPG 2 / Para 8b		Above Ground Storage Tanks If the filling operation is controlled from a place where it not reasonably practicable to see the tank or its vent pipe, the tank must be fitted with an automatic overfill protection device, which may include an alarm sounding device.
10.2.19	D&MG 14, / 9.3 b		The main switchgear shall be located in a non-hazardous area and incorporate the main isolation switch and the means of isolation. The main isolation switch must be labelled “Mains Isolating Switch” in the host nation language and English.
10.2.20	D&MG 14 / 9.3 g		Electrical supplies to Wet Stock Management and Leak Detection Systems, if fitted, must be fed by individual dedicated circuits. Miniature circuit breakers feeding such circuits are to be clearly labelled “Do not switch off” in the host nation language and English.
10.2.21	D&MG 14 / 9.5 r		A permanent label is to be fitted at all earthing and bonding connection points stating “Safety Electrical connection – Do not remove” in the host nation language and English.
10.2.22	D&MG 14 / 13.2 h		At unattended installations a notice stating the name, address and phone number of the person to be contacted in an emergency is to be displayed.
10.2.23	JSP 317		The Road Tanker Delivery Stand should be located in a safe, well ventilated position in the open and should offer a clear, unobstructed forward escape route.						FGSR Note: / Regulation / KPI
10.2.24	JSP 317		The Road Tanker Delivery Stand – Attended. Prior to a bulk receipt at an attended installation, the delivery driver must be presented with a notice detailing safe delivery/receipt and emergency procedures. The driver is to read and sign the notice to confirm they understand the procedures before commencing delivery.
10.2.25	JSP 317		The Road Tanker Delivery Stand – Unattended. Where supervision for tanker delivery is not provided, a notice shall be prominently displayed at the delivery point detailing safe delivery and USRP emergency procedures. Additionally, the road tanker driver should be specifically trained to deal with an emergency at the delivery stand during an unattended delivery.
10.2.26	JSP 317		The Road Tanker Delivery Stand. The delivery stand should be a minimum of 15m x 5m. If this isn’t practicable, signage and barriers are to be used to restrict vehicle and personnel access during transfer operations.
10.2.27	JSP 317		The Road Tanker Delivery Stand. Road tankers shall not be made to wait on public or internal busy roads. The delivery stand should be substantially level to ensure full extraction during deliveries.. If the delivery stand is in close proximity to an above ground storage tank, adequate protection against impact damage is to be provided.
10.2.28	JSP 317		The Road Tanker Delivery Stand must be impermeable to hydrocarbons and be capable of withstanding the axle weight of a fully laden delivery tanker.
10.2.29	JSP 317		The installation should have an effective means of both raising the alarm and giving warning in case of fire. It should be audible to all those likely to be effected by the fire. There must be access to a phone with in reasonable distance, which is to be clearly signposted.

10.3 FIRE, HEALTH & SAFETY					GRADING
					G	R		N/A	Remarks
Ref
10.3.1	JSP 317			Above ground storage tanks are to be marked with the correct NATO Product and Grade Identification markings. These markings must be visible from all directions.
10.3.2	JSP 317			Above ground Class I tanks shall be marked with ‘Highly Flammable, No Smoking, No Naked Lights’.
10.3.3	JSP 317			Above ground Class II tanks shall be marked ‘Flammable Liquid, No Smoking, No Naked Lights’.
10.3.4	JSP 317			Washing & changing facilities are to be provided for personnel at the place of work. In addition, the following items must also be provided: / Barrier Cream and After Work Cream. / Eyewash (In Date). / Emergency First Aid Kit.
10.3.5	JSP 317			Appropriate Personal Protective Equipment (PPE) and Respiratory Protective Equipment (RPE) is provided and used by all operators.
10.3.6	JSP 317			The quantity and location of all fire fighting equipment, which is determined by the Unit Fire Officer, must reflect what is stated in the Fire Safety Risk Assessment (FSRA).
10.3.7	JSP 317			An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan
10.3.8	JSP 317			Fire Safety Notices & Fire Action Notices must be displayed in order to comply with the Health and Safety (Safety Signs and Signals) Regulations 1996. Locations and quantities should relate to the local risks and be the result of a risk assessment.
10.3.9	JSP 317			Smoking or Smoking materials are not permitted in the hazardous area. Personnel are to deposit any smoking materials in a safe designated contraband area before entering a hazardous zone or likely hazardous area.
10.3.10	JSP 317			Grass and Vegetation is to be cut back to a minimum of 15m. Isolated deciduous trees are permitted but conifers must be removed. Grass cutting and removal of vegetation must be carried out iaw the MoD Safety Rules and Procedures for Work on Petroleum installations.
10.3.11	JSP 317			The following Hazard Warning Sign must be displayed on all approaches to the facility to clearly indicate the extent of the hazard. The sign must be produced in the local language and English:

10.4 ENVIRONMENTAL PROTECTION					GRADING
					G	R		N/A	Remarks
Ref
10.4.1		JSP 317		The following ‘Disconnect the Hose’ sign must be displayed at tanker Receipt/Issue points. The sign must be visible from the vehicle cab when the dispensing hose is connected to the installation:
10.4.2		JSP 317		Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
10.4.3		JSP 317		A Pollution Control Point (PCP) is to be established at the installation. The PCP must be clearly identifiable, stocked appropriately and be maintained on a regular basis.
10.4.4		JSP 317		Spillage Immediate Action Posters are to be prominently displayed at all Pollution Control Points and locations were F&L is stored.

10.5 OPERATING PROCEDURES					GRADING
					G	R		N/A	Remarks
Ref
10.5.1		JSP 317		Only authorised equipment, plant, vehicles or locomotives may enter the hazardous area.
10.5.2		JSP 317		Security. When not in use, all manhole covers, dip hatch covers, outlet points and dipsticks are to be locked. Keys are to be held in safe custody under local arrangements. This requirement may be waivered by the Fuels Officer in Charge if the dipsticks and sampling hatches are located inside a secure building.
10.5.3		JSP 317		A high standard of cleanliness is to be maintained at the installation. Rubbish of any kind must not be allowed to accumulate, and the growth of vegetation is to be controlled so as not to present a fire hazard.

11.	BULK WASTE INSTALLATION
		Waste F&L has the same impact on the environment as serviceable F&L. Therefore Bulk Waste Storage shall comply with principles laid down at JSP 317.				Information Only
11.1 OPERATION & FUNCTION			GRADING
			G	R	N/A	Remarks
Ref
11.1.1	JSP 317	Above Ground Storage Tanks- Secondary Containment The bund wall must be capable of retaining 110% of the largest container within the bund or 25% of the aggregate of multiple containers, whichever is greater.
11.1.2	JSP 317	Above Ground Storage Tanks- Secondary Containment The bund wall must: / Be impervious to liquid / Not normally be higher than 1.5m high. / Be fitted with crash protection if susceptible to impact damage e.g adjacent to a vehicle manoeuvring area.
11.1.3	JSP 317	Above Ground Storage Tanks- Secondary Containment. In order to prevent jetting; a phenomenon caused when the primary container fails and F&L is propelled at force beyond the secondary containment, the bund wall is not to be constructed too close to the tank.
11.1.4	JSP 317	Above Ground Storage Tanks - Secondary Containment The bund base and walls must not be penetrated by any valve, pipe or other opening which is used for draining the bund. Where a tank fill or draw off pipe must pass through the bund base or wall, the hole must be carefully sealed with a fire resistant seal to prevent oil escaping.
11.1.5	JSP 317	Above Ground Storage Tanks - Secondary Containment Rainwater which collects in the sump must be removed on a regular basis to ensure the bund capacity is maintained. This water is to be disposed of appropriately to ensure no pollution occurs.
11.1.6	JSP 317	Inspection of Bunds - Bunds should be regularly inspected for signs of damage and checked for water by the operator on a weekly basis.
11.1.7	JSP 317	Above Ground Storage Tanks - Secondary Containment If oil or a mixture of oil and water is found in the bund it must be disposed of in accordance with current Hazardous Waste Regulations.
11.1.8	JSP 317	Above Ground Storage Tanks - Small Tank Minimum Separation Distances. A small tank is considered to be a tank with a diameter of less than 10m. The minimum separation distances from site boundaries, fixed sources of ignition, buildings and process areas for single small tanks are as follows: / Tank Capacity (m³) Separation (m) / Less than or equal to 1 1* / Greater than 1 and less than or equal to 5 4 / Greater than 5 and less than or equal to 33 6 / Greater than 33 and less than or equal to 100 8 / *In this instance the tank must be sited at least 2m from doors, plain glazed windows, other openings or means of escape. In addition they must not be below any openings from an upper floor, regardless of vertical distance.
11.1.9	Oil Storage Regs 01 / 3 (3)	Above Ground Storage Tanks- Secondary Containment Valves should be as resistant to unauthorised interference and vandalism as far as is feasibly possible, with lockable or removable hand wheels.
11.1.10	OSR 01 / Reg 3(3)	Above Ground Storage Tank- Secondary Containment s All tank vent pipes, valves, filters, sight gauges and any other ancillary equipment with the exception of the fill pipe, draw off pipe or pump if the fuel has a flashpoint of less than 32ºc, must be positioned within the bund wall.
11.1.12	OSR 01 / Reg 3(3)	Above Ground Storage Tanks Valves should be marked to indicate whether they are open or closed, kept locked when not in use and fitted with a blanking cap or plug.
11.1.13	OSR 01 / Guidance Para 38	Above Ground Storage Tanks The connection point is to be located inside bund wall or be located in a position which allows for containment.
11.1.14	PPG 2 / Para 8b	Above Ground Storage Tanks If the filling operation is controlled from a place where it not reasonably practicable to see the tank or its vent pipe, the tank must be fitted with an automatic overfill protection device, which may include an alarm sounding device.
11.1.15	JSP 317	Above Ground Storage Tanks -Sight Glasses The use of sight glasses should be limited to the storage of Class II & III fuel tanks with a maximum capacity of 3500 Ltrs. If sight glasses are fitted they shall: / Be located in the secondary containment. / Be properly supported so that they cannot come loose. / Be fitted with a valve that automatically closes when the sight glass is not in use. / Be fitted with valves which are kept closed when not in use and only opened when taking contents readings.
11.1.16	JSP 317	The Road Tanker Delivery Stand should be located in a safe, well ventilated position in the open and should offer a clear, unobstructed forward escape route.				FGSR Note: / Regulation / KPI
11.1.17	JSP 317	The Road Tanker Delivery Stand – Attended. Prior to a bulk receipt at an attended installation, the delivery driver must be presented with a notice detailing safe delivery/receipt and emergency procedures. The driver is to read and sign the notice to confirm they understand the procedures before commencing delivery.
11.1.18	JSP 317	The Road Tanker Delivery Stand – Unattended. Where supervision for tanker delivery is not provided, a notice shall be prominently displayed at the delivery point detailing safe delivery and USRP emergency procedures. Additionally, the road tanker driver should be specifically trained to deal with an emergency at the delivery stand during an unattended delivery.
11.1.19	JSP 317	The Road Tanker Delivery Stand. The delivery stand should be a minimum of 15m x 5m. If this isn’t practicable, signage and barriers are to be used to restrict vehicle and personnel access during transfer operations.
11.1.20	JSP 317	The Road Tanker Delivery Stand. Road tankers shall not be made to wait on public or internal busy roads. The delivery stand should be substantially level to ensure full extraction during deliveries.. If the delivery stand is in close proximity to an above ground storage tank, adequate protection against impact damage is to be provided.
11.1.21	JSP 317	The Road Tanker Delivery Stand must be impermeable to hydrocarbons and be capable of withstanding the axle weight of a fully laden delivery tanker.

11.2 FIRE, HEALTH & SAFETY			GRADING
			G	R	N/A	Remarks
Ref
11.2.1	JSP 317	The quantity and location of all fire fighting equipment, which is determined by the Unit Fire Officer, must reflect what is stated in the Fire Safety Risk Assessment (FSRA).
11.2.2	JSP 317	An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan
11.2.3	JSP 317	Fire Safety Notices & Fire Action Notices must be displayed in order to comply with the Health and Safety (Safety Signs and Signals) Regulations 1996. Locations and quantities should relate to the local risks and be the result of a risk assessment.
11.2.4	JSP 317	Smoking or Smoking materials are not permitted in the hazardous area. Personnel are to deposit any smoking materials in a safe designated contraband area before entering a hazardous zone or likely hazardous area.
11.2.5	JSP 317	The following Hazard Warning Sign stating “Petroleum Mixture, Highly Flammable, No Smoking or Naked Flames, No Mobile Phones, No Parking” must be displayed on all approaches to the facility:
11.2.6	JSP 317	Grass and Vegetation is to be cut back to a minimum of 15m. Isolated deciduous trees are permitted but conifers must be removed. Grass cutting and removal of vegetation must be carried out iaw the MoD Safety Rules and Procedures for Work on Petroleum installations.

11.3 ENVIRONMENTAL PROTECTION			GRADING
			G	R	N/A	Remarks
Ref
11.3.1	JSP 317	Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
11.3.2	JSP 317	Spillage Immediate Action Posters are to be prominently displayed at all Pollution Control Points and locations were F&L is stored.				FGSR Note: Para 5 of example USRP.
11.3.3	JSP 317	The following ‘Disconnect the Hose’ sign must be displayed at tanker Receipt/Issue points. The sign must be visible from the vehicle cab when the dispensing hose is connected to the installation:
11.3.4	JSP 317	A Pollution Control Point (PCP) is to be established at the installation. The PCP must be clearly identifiable, stocked appropriately and be maintained on a regular basis.

11.4 OPERATING PROCEDURES			GRADING
			G	R	N/A	Remarks
Ref
11.4.1	JSP 317	Segregation. Different types of waste are to be stored separately to avoid the risk of fire, explosion or toxic vapour. Waste products should be collected and mixed into one of the following groupings as detailed in JSP 317, Part 3, Chapter 4, Annex A: / Mineral Oils / Fuel / Glycol’s, Glycol Ethers (AL’s) / The Bulk Waste Tank should be labelled with the specific group heading, prefixed by the word ‘Waste’ and followed by the word ‘Only’, e.g:
11.4.2	JSP 317	Only authorised equipment, plant, vehicles or locomotives may enter the hazardous area.
11.4.3	JSP 317	Security. When not in use, all manhole covers, dip hatch covers, outlet points and dipsticks are to be locked. Keys are to be held in safe custody under local arrangements. This requirement may be waivered by the Fuels Officer in Charge if the dipsticks and sampling hatches are located inside a secure building.
11.4.4	JSP 317	A high standard of cleanliness is to be maintained at the installation. Rubbish of any kind must not be allowed to accumulate, and the growth of vegetation is to be controlled so as not to present a fire hazard.

11.5 MAINTENANCE			GRADING
			G	R	N/A	Remarks
Ref
11.5.1	DIO / PG 06/12	The Bulk Waste Storage Tank has been inspected and deemed compliant by a competent member of the Maintenance Management Organisation in accordance with the requirements of the DIO Practitioners Guide 06/12.

12.	OIL PUMP ROOM & PRE

12.1 OPERATION & FUNCTION				GRADING
				G	R	N/A	Remarks
Ref
12.1.1	JSP 317		Containment. It is important to have means of controlling spillages and releases within the storage area to prevent the uncontrolled spreading of flammable liquids. The preferred option is that a 75-mm retention sill surrounds stores or the floor is recessed to this depth, / sloping towards a sump sized to contain the largest container stored within the room. An alternative approach would be to provide a 150-mm retaining sill without the provision of a sump, provided containment of the largest container is achieved. Sumps are not permitted to be connected to a drainage system.

12.2 FIRE, HEALTH & SAFETY				GRADING
				G	R	N/A	Remarks
Ref
12.2.1	JSP 317	Fire Safety Notices & Fire Action Notices must be displayed in order to comply with the Health and Safety (Safety Signs and Signals) Regulations 1996. Locations and quantities should relate to the local risks and be the result of a risk assessment.
12.2.2	JSP 317	Smoking or Smoking materials are not permitted in the hazardous area. Personnel are to deposit any smoking materials in a safe designated contraband area before entering a hazardous zone or likely hazardous area.
12.2.3	JSP 317	Where drums or other large containers are required to be moved by hand, cradles or trolleys are to be provided to minimise product spillage and injury to personnel.
12.2.4	JSP 317	The storage and handling of petroleum products is to be forbidden within 15m of any source of ignition.
12.2.5	JSP 317	A Hazard Warning Sign stating “Petroleum Mixture. Unauthorised Persons Prohibited Beyond This Point. No Smoking –No Naked Lights” must be displayed at the Oil Pump Room entrance.
12.2.6	JSP 317	An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan

12.3 ENVIRONMENTAL PROTECTION				GRADING
				G	R	N/A	Remarks
Ref
12.3.1	JSP 317	Spillages to be mopped up immediately using approved absorbent material which must be removed from the area for safe disposal after use.
12.3.2	JSP 317	Spillage Immediate Action Posters are to be prominently displayed at all Pollution Control Points and locations were F&L is stored.

12.4 OPERATING PROCEDURES				GRADING
				G	R	N/A	Remarks
Ref
12.4.1	JSP 317		Housekeeping. A good housekeeping standard is to be maintained. / Rubbish and refuse of any kind is to be removed.
12.4.2	JSP 317		Large Drums. Containers with a capacity of no greater than 200 Ltrs and intended for use on the same day or shift may be stored temporarily outside a pump room providing they are properly closed and labelled and the building wall is a fire wall.
12.4.3	JSP 317		Packed Products. Packed products for use in the pump room are to be stored in approved locations outside of the facility.

13.	GAS CYLINDER STORAGE FACILITIES [3]
[3] Unless otherwise stated all references for Sect 13 are extracted from JSP 319.
13.1 ADMINISTRATION / MANAGEMENT CONTROL					GRADING
				G			R	N/A			Remarks
Ref
13.1.1			2.1.1-8 / Para 49				Are current, regularly reviewed Standard Operating Procedures (SOPs) available (receipt, storage, issue)
13.1.2			2.1.10-6 / Para 47a				Is access to the compound restricted to authorised personnel? / Are these personnel competent to access the gas cylinder store? / (Records)
13.1.3			2.1.10-7 / Para 51				Are “Weekly Inspections” carried out? Records kept?					KPI H
13.1.4			2.1.10-7 / Para 48 / Para 52				Are “Receipt and Issue Checks” carried out detailing the following?
				Gas cylinder contents correctly identified.
				Gas cylinder is in date for its periodic inspection
				Lifed gas is in date / (e.g. Breathing / diving gases / ABO / medical gases certain toxic gases)					FGSR Note: / H&S
				Physical external check of cylinder body / label
				Cylinder Physical external check of Valve
				Cylinder accessories if fitted are secure & serviceable
				No leaks (method of leak checking Teepol, MGI, weight?)
				Certificates of Conformity available (as reqd)
				Cylinders accounted for / (e.g state board)
				Cylinders Secured / restrained and are (normally) stored in the upright position in specially designed pallets if provided / cylinders stowages					FGSR Note: / H&S
				Management control of the access keys to all gas cylinder compound / Is there an up to date list of authorised persons who may require access to the compound?
13.1.5			2.1.10-3 / Para 30(a)				Controlled Gases / Does the Cyl Compound Manager hold a record of Controlled (F) gases held in supply cylinders?					FGSR Note: / F-Gas Regs
13.1.6			2.1.10-3 / Para 30 / 2.1.10-6 / Para 47i				Controlled Gases / Does the Cyl Compound Manager hold a list of authorised F gas users who are trained to a nationally recognised qualification? / (the “user” shall demonstrate the evidence to the gas cylinder compound manager)
13.1.7			2.1.10-6 / Para 46j				Controlled Gases / Does the Cyl Compound Manager hold a record of quantities of Controlled (F) Gases recovered? (Recovery Cylinders as recorded on the label) / (Note if supply cyls are issued, there must be Recovery Cyls)
13.1.8			2.1.10-3 / Para 30 / 2.1.10-6 / Para 47i				Controlled Gases / Does the Cyl Compound Manager hold a record of Recovery Cylinders that have been returned to BOC?
13.1.9			2.1.10-3 / Para 30 / 2.1.10-6 / Para 47i, 47l				Controlled Gases / Controlled (F) gases. Is there a record of Controlled (F) gas leakages? (How? Visual? Teepol? Weight?)					FGSR Note: / F-Gas Regs

13.2 ADDITIONAL MANAGEMENT CONTROL -CONTROLLED GASES					GRADING
				G			R	N/A			Remarks
Ref
13.2.1		2.1.10-6 / Para 47j				Recovery Cylinders. Are empty, unused Recovery Cylinder Valves protected by shrink –wrap?
13.2.2		2.1.14-6 / Para 51				Recovery Cylinders. Has Manager ensured that operating unit has correctly annotated filled Recovery Cylinder with refrigerant gas type and weight on affixed table?

13.3 SITING					GRADING
				G			R	N/A			Remarks
Ref
13.3.1			1.7-1 / Para 6 / Para 11			Ventilation. Thorough ventilation by “clean” air required. Is the store located in an area where it may receive contaminated air e.g. aircraft jet efflux, or where there is substantial interference in the air flow from obstructions?
13.3.2			2.1.9-5 / Para 36			Underground power cables / “District” electrical cables shall not be routed through gas cylinder compounds. (Records –evidence of support) / (Electrical power cables may be routed through gas cylinder compounds that are used to supply the gas compound). See “design” below					(For new sites only)
13.3.3			2.1.9-3 / Para 20			Overhead power cables / Gas cylinder compounds shall not be located underneath electricity power cables or telephone lines.					Cables operating at a voltage <1.0 KV, cylinders to be >1.5m away (line drawn vertically down). / Cables operating at a voltage >1.0 KV, cylinders to be >10m away (line drawn vertically down). / (Identification of Power supply lines to be provided by competent person )
13.3.4			2.1.9-3 / Para 19			Is there a hazard from other infrastructure e.g. electrical installations, power cables (above and below ground), thermal radiation, and electromagnetic radiation?
13.3.5			2.1.9-3 / Para 18			Is the outdoor gas compound sited as a standalone compound? / (Segregation distances from compound fence to other recipients?)
13.3.6			2.1.9-7 / Para 57			Is there a space outside the storage area perimeter that is clear of all combustible material & vegetation to 3m?
13.3.7			2.1.9.8 / Para 62			Is the site located close to access routes for vehicles Armco barriers fitted?
13.3.8			2.1.9-6 / Para42			Is there a readily available telephone to aid emergency response within 50m of the gas compound?
13.3.9			2.1.9-9 / Para 47			Is there a readily available telephone to aid emergency response within 50m of the gas compound?

13.4 OPERATION & FUNCTION					GRADING
				G			R	N/A			Remarks
Ref
13.4.1				2.1.9-4 / Para 30	Lighting. Adequate lighting shall be provided to allow safe working activities in poor light conditions and to assist in the identification of cylinder types. Lighting is to be suitably protected. Not an ignition source.
13.4.2				2.1.9-5 / Para 34	Gas compound facility (e.g. fencing, gates, and pipework) to be adequately earthed, based on Risk Assessment (Recorded, evidence).
13.4.3				2.1.9-5 / Para 30	Gas compound facility (e.g. fencing, gates, and pipework) to be protected against static electricity, based on Risk Assessment (Recorded, evidence).
13.4.4				2.1.9-5 / Para 32-33	Is the compound secure? Fenced/permanent walls at least 1.8m in height. Secure access gates.
13.4.5				2.1.9-5 / Para 39	Do access doors open outwards and have the correct security locks?
13.4.6				2.1.9-6 / Para 43	Gas monitoring. Gas detection equipment shall be installed unless Risk Assessment can mitigate that the largest foreseeable escape of particular gas will cause no danger to health of persons or damage to environment. (Records, evidence). / (e.g. Asphyxiant, Toxic, F-gas, oxygen enrichment)					FGSR Note: / H&S
13.4.7				2.1.9-6 / Para 44	Outdoor Gas Storage compound to be well ventilated. / a. No more than 50% of perimeter walls to be obstructed by solid walls. / (Where practicable solid walls should be on opposite sites). / (Open wire mesh or steel louvers are suitable for use as free venting sides) / (Low level ventilation for heavier than air gases) / b. Roof if fitted / (e.g. slatted roofs lighter than air gases)					FGSR Note: / H&S / KPI F
13.4.8				2.1.9-6 / Para 36-38	If barriers are constructed within the compound; / Cylinders stored against barriers / partitions (if constructed)
13.4.9				2.1.9-4 / Para 29	Cylinders to be smaller (shorter) than barrier
				Barrier height 2m (minimum)
				Barriers to be constructed from fire resistant material
				Is the compound constructed from non-combustible materials?					FGSR Note: / H&S / KPI F
13.4.10				2.1.9-3 / Para 22	Is the compound floor flat & constructed from concrete or other non-porous material?
13.4.11				2.1.9-3 / Para 24	Does the floor have a suitable runoff to remove rainwater
13.4.12				2.1.9-4 / Para 25	Is the drainage system designed to prevent contaminants entering other controlled drainage / soakaways or Controlled waters? / (e.g. fitment of suitable gas trap in drain)					FGSR Note: / Env / H&S
13.4.13				2.1.9C / Anx C	Is the compound correctly sign-posted? Hazard(s) identified. Emergency actions detailed. / Boundary warning signs and pictograms shall be clearly visible from all angles of approach. / All gas storage sites shall display the following signs/pictograms/notices on the access point and boundary fence or wall: / a. Danger – explosive gases. / b. No smoking. / c. No naked flames. / d. No mobile phones. / e. No access to unauthorised personnel. / f. No storage of oil, grease or combustible materials / The appropriate diamond hazard labels shall also be displayed. However, if the stored gases would require more than two subsidiary diamond hazard labels, the primary diamond hazard label(s) should be used instead. / Examples below:					KPI A
Additional requirements for internal storage industrial cylinders
13.4.14				2.1.9-9 / Para 73	Construction – evidence of construction of non-combustible materials. / When part of a larger building, internal store shall be separated from rest of building by firewall (fire resistant)
13.4.15				2.1.9-9 / Para 73a	Construction - Explosive Relief. One wall or the roof must be made of open mesh or lightweight friable material to provide explosive relief. / Relief partition to be designed so that any explosion would vent safely without producing dangerous projectiles (Recorded, evidence).
13.4.16				2.1.9-12 / Para 89	All equipment / fittings lighting within the internal storeroom. Is it applicable to the gas hazard stored? (e.g. ATEX- flammable gases) / e.g. Is it & designed &maintained
13.4.17				2.1.9-11 / Para 81	Construction. If indoors, as a compartment within a single story building, with at least one external wall.
13.4.18				2.1.9-9 / Para 73a-e	Gas detection. Is Atmospheric Monitoring provided? Is there a serviceable alarm (flashing lights, alarms) both inside & outside the store? Evidence of serviceablity of system / calibration?					FGSR Note: / H&S
13.4.19				2.1.9.9-11 / Para 80	Ventilation. Does it have thorough ventilation to a safe place / 12 air changes per hour minimum? (Recorded, evidence) Evidence of serviceablity of system / calibration?					FGSR Note: / H&S
13.4.20				2.1.9.9-11 / Para 78	Forced ventilation. Serviceable LEV system must be alarmed to warn of failure / (Recorded evidence) Evidence of serviceablity of system / calibration?					FGSR Note: / H&S
13.4.21				2.1.9.9-11 / Para 77	Ventilation. Buildings containing flammable gases to have openings >= 2.5% of the combined area of the walls & roof of the room / Or 12% of the area of one of the external walls / Whichever the greater. (Recorded, evidence)					FGSR Note: / H&S
13.4.22				2.1.9.9-11 / Para 80	Very Toxic gas cylinders shall not be stored in internal storage					FGSR Note: / H&S
13.4.23				2.1.9.9-11 / Para 85	Pyrophoric cylinders shall not be stored in internal storage					FGSR Note: / H&S
13.4.24				2.1.9.9-11 / Para 85	Pyrophoric cylinders shall not be stored in internal storage					FGSR Note: / H&S

13.5 FIRE, HEALTH AND SAFETY					GRADING
				G			R	N/A			Remarks
Ref
13.5.1				2.1.9-8 / Para 59		Is the available fire fighting equipment as per the Station Fire Officers recommendations? / Minimum of 2 x extinguishers for a Class C fire (gases or liquefiable gases). / For flammable gases these to be 2 x 9 kg dry powder fire extinguishers.					KPI J
13.5.2				JSP 317		An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan
13.5.3				2.1.9-7 / Para 55		Are fire posters and emergency evacuation posters available, in good condition and up-to-date? Located at all entry points.					KPI 2 A
13.5.4				2.1.9-8 / Para 63		Smoking is not permitted within 3m of the storage facility. Signage.
13.5.5				2.1.1-8 / Para 48		First Aid Boxes / Have they been provided? / Are they maintained / serviceable? / Are First aid box locations identified? / Are First Aiders clearly identified? / Is signage adequate and correct?
13.5.6				2.1 Ch7		Is manual handling equipment available – e.g. cylinder trolleys? Are they of the correct size and type? / Is it of the correct type / Is it serviceable? / Risk Assessment - Records – Evidence? / e.g. If Fork Lift Trucks are employed are they suitable for use in this environment? (Atex Compliant- flametec in explosive atmos?)					KPI G
13.5.7				2.1 ch 2 / JSP 375, / Part 2 Ch 15		Do all personnel have their own suitable PPE? / Is it in good condition? / Is it stored correctly, maintained and inspected? / PPE. Is PPE applicable for hazards identified from R.A? / e.g. manual handling, safety footwear, gloves and eye/face protection. / Cryogenics / LPG. / Toxics / Separate clean, grease free PPE / clothing for oxygen					KPI H

13.6 STORE ORGANISATION					GRADING
				G			R	N/A					Remarks
Ref
13.6.1	2.1.10-1 / Para 2-10 / 2.1.10-5 / Para 40					Is there appropriate segregation? Are these segregated areas signposted?
				Full and empty cylinders separated.
				Hazard groups (flammable/oxidising/inert/toxic etc.) separated. / Cylinders of the same hazard group shall remain together
				LPG cylinders separated.
				Unserviceable cylinders separated.
				Medical cylinders separated. (In separate storage facility)
				Note: Nominally empty cylinders to be treated as full for zoning and separation distance calculations
				Is there sufficient room to allow safe movement of personnel and any mechanical aids? / Minimum isle size 0.6 m.
13.6.2	2.1.10-7 / Para 48 (e-g)					On all cylinders (including nominally empty cylinders) the valve is to be closed. The valve outlet is to be protected.
13.6.3	2.1.10-7 / Para 48f					Cylinders to be vertically stacked / (Unless specifically designed to be belly stacked)
13.6.4	2.1.10-2 / Para 13					Only the minimum quantity of cylinders necessary are being stored. Nominally empty, unwanted or unserviceable cylinders are returned promptly.
13.6.5	2.1.10-2 / Para 19					The provision of a device to indicate wind direction is to be considered, based on R.A.
13.6.6	2.1.11-3 / Para 16d					Is the site of an adequate size for the quantity and type of cylinders being stored?
13.6.7	2.1.9-5 / Para 40 / Para 42					Vehicles & pedestrians routes segregated & marked
13.6.8	2.1.9-5 / Para 40 / Para 42					No sharp bends corners, blind areas, restrictive height for vehicle movements
13.6.9	2.1.9-6 / Para 43					Is access adequate for delivery vehicles including emergency escape routes, identified and clear? / (Other vehicles prohibited parking in delivery lorry drop off / collection points)					FGSR Note: / H&S / Regulation – Condition of Certification

14.	CRYOGENIIC LIQUID STORAGE FACILITIES[4]
[4] Unless otherwise stated all references for Sect 14 are extracted from JSP 319.
14.1 ADMINISTRATION MANAGEMENT CONTROL					GRADING
				G			R		N/A			Remarks
Ref
14.1.1	2.1.1-8 / Para 49 / 2.1.11-16 / Para 119			Are current, regularly reviewed Standard Operating Procedures (SOPs) available (receipt, storage delivery)
14.1.2	2.1.11-14 / Para 105 / Table 3			MOD owned aviation cryogenic storage tanks. / Maintenance policy iaw Air Publication system. / 2400 L Tank (Mk1 Mk2) / 4000 L Tank / 9000 L Tank / 18000 L Tank / Is the plant serviceable)					FGSR Note / PSSR / Aviation Engineering lead – However operators shall demonstrate JAP / MAP compliance (MF731 Labels, MF707 )
14.1.3	2.1.11-15 / Para 109			Contractor owned aviation cryogenic storage tanks (BOC) / Maintenance policy of tank with Contractor. (Evidence – Records)					FGSR Note / PSSR
14.1.4	2.1.11-15 / Para 111 a-g			Identification of exact point at which the Contractors responsibility ends & MODs / DIO begins, / To be demonstrated in written procedures / SOPs and physically on plant / infra.					FGSR Note: / H&S MHSWR-4Cs
14.1.5	JSP 375 Pt 2 Ch 29			Cryogenic liquid storage compounds: System to be maintained iaw PSSR 2000. (evidence of WSE etc)					FGSR Note / PSSR
14.1.6	2.1.11-2 / Para 12			Confined Spaces- Adjacent Spaces to Cryogenic Liquid Storage Compound. / Permit –to- Work / Standing Instruction, suitable Risk assessment required to enter inspection pit, cable ducts, wells or other confined space adjacent to an installation storing cryogenic liquids. (Drains / confined spaces -15m from tank) / (Evidence- Records) / Signage on adjacent spaces?
14.1.7	2.1.11-9 / Para 65			Emergency Shower Use of emergency shower & emergency service response is to be included in SOPs
14.1.8	2.1.11-9 / Para 65			Cryogenic liquid storage compounds. Emergency Shower maintenance, inspection, & testing (records, evidence) / a. 1 monthly visual inspection, Flush, verification of proper operation of & testing of the alarm system. / b. Annual clearing inspection & compliance assessment.
14.1.9	PSSR 2000			Has the site completed a current BOC Audit Checklist Third Party Owned Vessels (BOC Form GERTL002)

14.2 SITING (LOx sites – other cryogenic liquids treated same)					GRADING
				G			R		N/A			Remarks
Ref
14.2.1	Part 1 Ch 7 / 2.1.11-2 / Para 15					All new installations, or substantial changes to a site, are subject to a Siting Board. Recorded? Signed off by all parties? / (also part of handover check)
14.2.2	2.1.11-4 / Para 19					New LOx sites, a minimum safety distance of 1500m from any other area of risk is recommended. If not feasible then: / Local protection around site to prevent unauthorised access. / Prevention of contamination entering the site. / Risk assessment of dynamic movement of Cryogenic storage compound – potential liquid. / vapour cloud migration / (Unit to demonstrate RA carried out) / (also part of handover check)
14.2.3	2.1.11-2 / Para 11					Ventilation. Thorough ventilation by fresh uncontaminated ambient air – separation may have to be greater than separation distances listed below. / e.g. consideration against aircraft jet exhaust fumes / (also part of handover check)
14.2.4	2.1.11-3 / Para 16 d					Provision of wind direction indication (e.g. windsock)?
14.2.5	Table 2.1.11.1 / (STANAG 7175 / BCGA COP 36) / Most conservative					Safety distances from cryogenic storage tank to:
				Public roads / railways 50m
				Flammable liquid / gases storage 25m
				Aircraft parking, refuel / defuel 25m
				Traffic Routes 15m
				Parked Vehicles 15m
				Combustible solid materials 15m
				Inlet to sewage system / drains 15m / Inlet to underground conduits
				Buildings 15m
				Aircraft Taxiways 15m
				Asphalt / tar based surface 15m
				Uncultivated land 15m
				Property Boundary 15m
				Battery operated / Non intrinsic electrical devices 15m
				Fire, open flame, smoking areas 15m
				VHF UHF radio 15m
				HF radio 70m
				Bowman radio 70m
14.2.6	2.1.11-3 / Para 16f					Cryogenic Liquid Storage Compounds shall not be sited directly under electricity or phone cables
14.2.7	2.1.11-7 / Para 40					Cryogenic Liquids boil off pit. Located away from windows, doors, escape exits.
14.2.8	2.1.11-7 / Para 41					Cryogenic Liquids boil off pit. Free from contaminants. No carbonaceous materials present? (e.g. leaves, oils, grasses)
14.2.9	2.1.11-7 / Para 39					Cryogenic Liquids boil off pit. (Subj to RA). Dependant on spillages into pit, the pit may need to be considered as a confined space. / If so, Barriers, warning signs shall be fitted

14.3 OPERATION & FUNCTION					GRADING
				G			R		N/A			Remarks
Ref
14.3.1		2.1.12-6 / Para 39			Oxygen enrichment of air. Low temperatures – bulk LiN, Liquid Helium. / LOx may be precipitated out, of the atmosphere when handling LiN & Liquid Helium. / Cryogenic liquid storage compounds storing LiN, Liquid Helium to be RA for oxygen enrichment / ( NO OILS GREASES PRESENT, OXYGEN COMPATIBLE PRODUCTS USED)
14.3.2		2.1.11-8 / Para 52			Oxygen compatible PTFE tape – NSN 71a-8030-99-5624616 shall be used on cryogenic liquid systems (sparingly)
14.3.3		2.1.11-5 / Para 22			Construction of Cryogenic liquid storage compounds. / No combustible material to be used in the construction of compound.
14.3.4		2.1.11-6 / Para 25			Construction of Cryogenic liquid storage compounds. / Walls to be of solid construction (plasterboard not recommended). Internal rough brick / block work shall be coated with smooth coat of gypsum / lime based plaster.
14.3.5		2.1.11-5 / Para 24			Construction of Cryogenic liquid storage compounds. / Floor shall be solid construction, non-combustible materials. / Floor to be sloped (1:80 - 1:100) to safe area (away from storage tanks, compound entrance) - towards boil off pit.
14.3.6		2.1.11-7 / Para 47			Construction of Cryogenic liquid storage compounds. / Floor - asphalt / Tarmac surfaces shall not be used. / Recommend concrete surface with oxygen compliant silicone based jointing compound.
14.3.7		2.1.11-5 / Para 21			Construction of Cryogenic liquid storage compounds. Enclosed or semi enclosed spaces covering cryogenic tanks. (Dutch Barns) / Specific Risk Assessment to be carried out. (Forced ventilation, blast relief panels/ roofs etc) / (also part of handover check)
14.3.8		2.1.11-6 / Para 29			Construction of Cryogenic liquid storage compounds. Boundary/ security. / Fence to be open type (chain link or similar) – restrict entry to unauthorised personnel & be 1.8m high.					FGSR Note: / H&S
14.3.9		2.1.11-6 / Para 27-32			Construction of Cryogenic liquid storage compounds. / Boundary fence to have 2 access points. / Gates to be of similar construction to fence. / 2nd emergency exit min 0.8m wide.
14.3.10		2.1.11-6 / Para 27-32			Main gate to have 2 wings, each min 0.6 m wide
14.3.11		2.1.11-6 / Para 31			Emergency exit to open in direction of escape / Emergency exit to be fitted with panic furniture (lock type not requiring key, card, or code for opening). / Escape means to be unobstructed
14.3.12		2.1.11-6 / Para 33			Road tanker –safe unrestricted access/ egress					FGSR Note: / H&S / Regulation – Condition of Certification
14.3.13		2.1.11-6 / Para 34			Tanker operator should have clear line of sight to see both delivery tanker & cryogenic storage vessel					Regulation – Condition of Certification
14.3.14		2.1.11-6 / Para 34 / BCGA COP 36			Cryogenic liquid storage compounds A concrete apron beneath the rear of the tanker is parked is required.					Regulation – Condition of Certification / KPI
14.3.15		2.1.11-6 / Para 35			Cryogenic liquid storage compounds. The liquid transfer area shall be designated a “No parking area” / (annotation signage, marking)
14.3.16		2.1.11-6 / Para 36			Cryogenic liquid storage compounds. Protective barriers (kerbs , bollards) are to be installed around cryogenic storage tanks to prevent vehicular impact					FGSR Note: / H&S
14.3.17		2.1.11-12 / Para 90			Cryogenic liquid storage compounds. Pipelines. / Connection fittings of multistorage installations, pipework connecting storage tanks, or long fill lines are to be clearly marked with the gas name or symbol. / Marking / labelling is to be at the inlet /outlet & approximately 2m intervals
14.3.18		2.1.11-8 / Para 59			Cryogenic liquid storage compounds. Pressure Gauges. / All pressure gauges used for liquid / gaseous oxygen shall have dials inscribed “OXYGEN” and “TESTED WITHOUT OIL” or “OIL FREE”. / Example (oil can crossed out = oil free)
14.3.19		2.1.11-9 / Para 63			Cryogenic liquid storage compounds. Emergency Shower. / Drench type shower with eye bath shall be installed.					HH
14.3.20		2.1.11-9 / Para 68			Cryogenic liquid storage compounds. Emergency Shower. / Shower to be located such to avoid impeding normal operations. / Water to drain away as not to form ice (contact with cryogenic liquids)
14.3.21		2.1.11-9 / Para 64			Cryogenic liquid storage compounds. Emergency Shower / Automated alarm system shall be attached to the shower & connected to appropriate recipient (e.g. guardroom, medical centre)
14.3.22		2.1.11-9 / Para 66			Cryogenic liquid storage compounds. Emergency Shower. / Water supply – clean potable / Water supply – flow for 15 mins uninterrupted / Water supply – maintained above 0° C, below 20°C.
14.3.23		2.1.11-9 / Para 69			Cryogenic liquid storage compounds. Emergency Shower. Relevant symbol or pictogram to be clearly displayed.
14.3.24		2.1.11-12 / Para 88 -89			Cryogenic liquid storage compounds. Signage / Entrance to the compound to have the following cryogenic signs displayed. / NO SMOKING / NO NAKED LIGHTS / NO STORAGE OF OIL, GREASE OR COMBUSTIBLE MATERIALS / EXTREME COLD HAZARD / AUTHORISED PERSONS ONLY / NO MOBILE PHONES / NO STEEL TIPPED SHOES / BOOTS / For cryogenic (LOx) storage compounds / LIQUID OXYGEN / OXIDISING SUBSTANCE / For liquid nitrogen / argon / helium storage compounds / LIQUID NITROGEN (ARGON / HELIUM) as appropriate / ASPHYXIATION HAZARD
14.3.25		2.1.11-12 / Para 87			Cryogenic liquid storage compounds. Signage / A shall be displayed detailing the specific action to be taken in the event of an emergency detailing: / WHOM TO CONTACT / EMERGENCY CONTACT DETAILS / CONTACT DETAILS OF CRYOGENIC LIQUID SUPPLIER / CRYOGENIC LIQUID SUPPLIER EMERGENCY 24 HR NUMBER
14.3.26		2.1.11-12 / Para 87			Cryogenic liquid storage compounds. Signage / At the entrance to the site, the appropriate fire signs & notices are to be displayed (Fire Action Notice)
14.3.27		2.1.11-12 / Para 89			Cryogenic liquid storage compounds. / Each individual tank shall be clearly labelled with its contents & associated UN Number. / LIQUID OXYGEN UN1073 / LIQUID NITROGEN UN 1977 / LIQUID ARGON UN 1951
14.3.28		2.1.11-11 / Para 79 / Para 154 / BS-EN / 5958-2			Earthing: Evidence that all metal fitments / joints in Cryogenic Liquid Storage Compound are adequately earthed (10Ω)? / (Records?)
14.3.29		2.1.11-7 / Para 38			Cryogenic Liquids boil off pit. Dedicated area to facilitate safe evaporation of spillage of cryogenic liquid. / (Size: Not needed for 110% tank capacity, but for foreseeable spills)
14.3.30		2.1.11-7 / Para 39			Cryogenic Liquids boil off pit Constructed with oxygen compatible non porous materials that will not cold brittle fracture
14.3.31		2.1.11-7 / Para 42			Cryogenic Liquids boil off pit. Pit shall be totally independent of soakaways used to intercept F&L spillages and surface water runoff from aircraft aprons & runways.

14.4 OPERATING PROCEDURES					GRADING
				G			R		N/A			Remarks
Ref
14.4.1		2.1.12-10 / Para 80	Personnel who have worked in an oxygen enriched atmosphere (delivery, transfer) shall not smoke; go near heat sources / naked flames, until they have ventilated their clothing for 15 mins. Written Procedures?
14.4.2		2.1.11-8 / Para 54- 55	All joints on hoses / coupling shall not be unduly tightened when the parts are cold soaked. To rectify leakages. (leaks can be detected by an accumulation of ice around area) / Hammers shall not be used on cold soaked joints couplings; the correct “C” spanner shall be used.
14.4.3		2.1.12-8 / Para 64	Safety Man. / Safety Man shall be correctly dressed & present during cryogenic liquid transfer (delivery / transfer) Written Procedures?
14.4.4		2.1.12-8 / Para 66	Safety Man / Safety Man not to be involved in the activity Written Procedures?
14.4.5		2.1.11-10 / Para 70-71	Gas monitoring. Gas detection equipment shall be installed unless Risk Assessment can mitigate that the largest foreseeable escape of particular gas will cause no danger to health of persons or damage to environment. (Records, evidence). / (e.g. Asphyxiant, Toxic, F-gas, oxygen enrichment)
14.4.6		2.1.11-8 / Para 56	LOx equipment / personal. Hydrocarbon based oils greases, soaps shall NOT be used within the cryogenic liquid storage compound. / (e.g. no evidence of grease in valves, oily PPE, no food)

14.5 FIRE HEALTH & SAFETY					GRADING
				G			R	N/A			Remarks
Ref
14.5.1		2.1.11-17 / Para 130		If industrial gas cylinders are stored inside a specially constructed room within a building a bespoke risk assessment is required. (recorded, evidence)
14.5.2		JSP 317		An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan
14.5.3		2.1.9-7 / Para 55		Are fire posters and emergency evacuation posters available, in good condition and up-to-date? Located at all entry points.					KPI 2 A
14.5.4		2.1.11-17 / Para 130		Construction – evidence of construction of non-combustible materials. / When part of a larger building, internal store shall be separated from rest of building by firewall – 60 mins fire resistance.
14.5.5		2.9.4.02 - 2.9.4.03		Construction. If indoors, as a compartment within a single story building, with at least one external wall.
14.5.6		2.1.11-10 / Para 70		Gas detection. Is Atmospheric Monitoring provided? Is there a serviceable alarm (flashing lights, alarms) both inside & outside the store? Evidence of serviceablity of system / calibration?					HH
14.5.7		2.1.11-11 / Para 74		Ventilation. Does it have thorough ventilation to a safe place / max O2 23.5% min O2 19:5% - Evidence of serviceablity of system / calibration?					HH
14.5.8		2.1.2-4 / Para 25 / Annex A		PPE be solely of LOx usage. Clean – oil free.					KPI

15.	BULK LPG STORAGE FACILITIES[5]
[5] Unless otherwise stated all references for Sect 15 are extracted from JSP 319.
LPG Tank Capacity……………(L) (Water capacity) / ………………………………..(kg/ Tonnes) / LPG Tank Owner……………………….Facility RPC………………………….Single or Group……… / Tank Serial No(s)……………………………. / Firewall YES NO / Conversion Water Capacity / X L x 0.509 = Tonnes / 1000 X Tonnes x 1000 = Litres / 0.509 / Nominal LPG capacity = 87% of tank size (ullage)
15.1 ADMINISTRATION / MANAGEMENT CONTROL					GRADING
					G	R	N/A	Remarks
Ref JSP 319
15.1.1				2.1.1-8 / Para 49				Are current, regularly reviewed Standard Operating Procedures (SOPs) available for operator compound entry.
15.1.2				2.2.4-2 / Para 24-49 / DIO IN 03/13				Demarcation of responsibility of ownership of management of Bulk LPG vessel / supportive structure and pipework to be clearly defined and recorded in writing and understood by all parties. Point of isolation to be clearly identified. (e.g. output of 1st Stage Regulator)				FGSR Note: / H&S MHSWR-4Cs –Imp Notice / KPI H / (also part of handover check)
15.1.3				2.2.3-2 / Para 24-49 / 2.2.6-1 / Para / 2.2.8-4 / Para 13 / DIO GSC Pt 3				LPG Compounds access for maintenance / Only Competent / Authorised Personnel shall enter LPG Bulk Storage Compounds – Maintenance; Cyl Contractor – competent, MMO, RPC, SETL / (P t W / Standing Instructions SI. Any specific training required from Contractor?(RPC Competent) P t W / SI				FGSR Note: / H&S - Imp Notice / Note JSP 375 Vol 3 Chap 5 no longer includes LPG, however, / “4Cs” “Employer” responsibilities to “Contractors” is mandated in HASAWA sect 2 & 3 / Permit to Work covered in HSG 250-Guidance to Permit to Work Systems / SI mandated in JSP 375 Vol 3 Ch 5 Sect 5.9
15.1.4				2.2.4-2 / Para 24-49 / DIO GSC PG 2015/01, / JOB 11.2				The LPG Storage Vessel – maintenance SETL / MMO / RPC to demonstrate that that the LPG tank has been maintained.				FGSR Note: / PSSR- WSE – Imp Notice / Tank Owner is responsible for examination & maintenance of LPG storage vessel up to first stage regulator – However, MMO SETL, RPC; need to have date recorded / aware for maintenance (4Cs).
15.1.5				2.2.4-2 / Para 24-49 / DIO GSC PG 2015/01, / JOB 11.2				The Bulk LPG Compound / SETL /MMO /RPC is responsible for examination & maintenance of the LPG compound from the output of the first stage regulator (not the LPG storage vessel). To be demonstrated - Recorded.				FGSR Note: / H&S - Imp Notice
15.1.6				2.2.4-8 / Para 46 / UK / LPG COP 1 Para 5.1.4 / DIO GSC PG 2015/01, / JOB 11.2				Electrical certificates (if applicable) to be provided for installation:- / Identifying type of inspections required (supply, bonding, earthing) / Periodicity of inspection (not exceed 12m)				FGSR Note: / Regulation
15.1.7				2.2.4-8 / Para 49 / UK / LPG COP 1 Para 5.2.(b				LPG Storage Vessel >1 Tonne capacity to be permanently bonded to an effective earthing point. (evidence of testing)				FGSR Note: / H&S - Imp Notice
15.1.8				2.2.4-8 / Para 48 / UK / LPG COP 1 Para 5.2.(b)				LPG Storage Vessel up to 1 Tonne capacity to be bonded to an effective earthing point. Must be demonstrated to be conductive (leg lug, corrosion free, paint free).
15.1.9				UK / LPG COP 1 Para 2.6.1				Compound security. Installations individual tank > 4 Tonnes require specific R.A / On unsecure sites only

15.2 SITING					GRADING
					G	R	N/A	Remarks

15.2.1				2.2.8-3 / Para 11i			Storage Vessels not to be sited directly under electricity or phone cables					(also part of handover check)
15.2.2				Tables 2.2.-8 / Anx A			Power cables less than 1.0 KV (including telephone cables) to be 1.5m from storage vessels (from plane drawn vertically down onto ground) / Power cables greater than 1.0KV to be 10m from storage vessels (from plane drawn vertically down onto ground) / (Identification of Power supply lines to be provided by competent person from site)					(also part of handover check)
15.2.3				2.2.8-3 / Para 11i			Storage Vessels not to be sited directly under overhanging trees					(also part of handover check)
15.2.4				2.2.8-3 / Para 11i			Storage Vessels not to be sited directly under roof eves					(also part of handover check)
15.2.5				2.2.8-3 / Para 11j			Storage Vessels not to be sited where damage from overhead structures may occur (cranes, gantries)					(also part of handover check)
15.2.6				2.2.8-3 / Para 11m			No underground services to pass under the foundations of LPG storage vessels. (Records, evidence of support).					(also part of handover check)
15.2.7				2.2.8-1 / Para 4			Topography of ground level, well drained open ventilated areas / Note - Where LPG vessels have replaced oil tanks in a bunded facility, ensure that existing bund does not restrict ventilation.					(also part of handover check)
15.2.8				Table 1 2.2.-8 / Anx A			Multiple vessel bulk LPG installation-Individual Tank up to 4 Tonnes – minimum separation between vessels 1m. >4 Tonnes 1.5m					(also part of handover check)
15.2.9				Tables 2.2.-8 / Anx A			Separation from hazardous substances. Flammable liquids (<32°C irrespective of quantity). / LPG vessel (<=60 Tonnes) 6m from LPG storage vessel to bund wall of Flammable Substance. / LPG vessel (>60 Tonnes) 15m from LPG storage vessel to bund wall of Flammable Substance.. / (Separation distances with nil firewall)					FGSR Note: / H&S - Imp Notice / (also part of handover check)
15.2.10				Tables 2.2.-8 / Anx A			Separation from hazardous substances. Flammable liquids (>32°C <65°C) up to 3000L / LPG vessel (<=60 Tonnes) 3m from LPG storage vessel to bund wall of Flammable Substance. / LPG vessel (>60 Tonnes) 6m from LPG storage vessel to bund wall of Flammable Substance. / (Separation distances with nil firewall)					FGSR Note: / H&S - Imp Notice / (also part of handover check)
15.2.11				2.2.8-2 / Para 11b / Tables 2.2.-8 / Anx A			Separation from hazardous substances. Flammable liquids (>32°C <65°C) >3000L / LPG vessel (<=60 Tonnes) 3m from LPG storage vessel to bund wall of Flammable Substance. and 6m to tank / LPG vessel (>60 Tonnes) 15m from LPG storage vessel to bund wall of Flammable Substance. / (Separation distances with nil firewall)					FGSR Note: / H&S - Imp Notice / (also part of handover check)
15.2.12				2.2.8-2 / Para 11b / Tables 2.2.-8 / Anx A			Separation from Liquid Oxygen (LOx) Storage tanks. / LPG vessel (0.1 - 1.1 Tonnes) 6m / LPG vessel (1.1 – 4.0 Tonnes) 7.5m / LPG vessel (4.0 – 60.0 Tonnes) 15m / LPG vessel (60.0 – 150.0 Tonnes) 22.5m / (Separation distances with nil firewall)					FGSR Note: / H&S - Imp Notice / (also part of handover check)
15.2.13				2.2.8-2 / Para 11b / Tables 2.2.-8 / Anx A			Separation distance for: / Powered vehicles / Buildings / boundary / combustible material / LPG vessel (150 -500L) (0.05 – 0.25 Tonnes) (Grp 0.8 Tonnes) 2.5m / LPG vessel(501-2500L) (0.25 – 1.1 Tonnes) (Grp 3.5 Tonnes) 3m / LPG vessel (2501-9000L) (1.1- 4.0 Tonnes) (Grp 12.5 Tonnes) 7.5m / LPG vessel (9001- 135kL )(4.0 - 60 Tonnes) (Grp 200 Tonnes) 15m / (Separation distances with nil firewall - Single tank Size sep dist / Group Sep dist in italics ) / Weeds long grass deciduous shrubs: / <2 Tonnes as Sep Dist / > 2 Tonnes 6m (uklpg CP 1, 2.3.1.10)					FGSR Note: / H&S - Imp Notice / Use value recorded on data plate / (also part of handover check)
15.2.14				2.2.8-2 / Para 11b / Tables 2.2.-8 / Anx A			Is LPG installation located within vicinity of other dangerous goods storage? (e.g. explosive sites) / If so; has site owner referred to other DG standard to identify safety distance? (other domains e.g. JSP 862)					(also part of handover check)
15.2.15				2.2.8-3 / Para 11b			Storage Vessels to be away from aircraft taxiways / If so, has site owner referred to safety distances mandated by aircraft type?					(also part of handover check)
15.2.16				2.2.8-3 / Para 11p			Presence of evaporation area. / (gravelled area can encompass whole of site)
15.2.17				2.2.8-1 / Para 4			Storage vessels – no presence of open pits / hollows / round depressions within safety distances
15.2.18				2.2.8-3 / Para l			No open drains, gullies or ducts shall be located within the LPG storage vessel safety distances unless orifices are protected from LPG vapours					FGSR Note: / H&S - Imp Notice

15.3 OPERATION & FUNCTION					GRADING
					G	R	N/A	Remarks
Ref
15.3.1			DIO IN 03/13 / DIO SA 01/12 / HSG INDG 428			Underground LPG pipework / SETL /MMO / RPC is responsible for examination & maintenance of the LPG pipework from the first stage regulator (not the LPG storage vessel) including underground pipework downstream. To be demonstrated - Recorded. / (Strategy of steel underground pipelines replaced, 30m of buildings)
15.3.2			2.2.8-2 / Para 9 a-c / UK / LPG COP 1 Para 2.6.1			Compound security. 1.8m fence with adequate through ventilation / (If the LPG Installation has no Security fence, and no specific risk assessment has been produced to mitigate this risk; a “Red” grade must be awarded for this question). / If a specific Risk assessment has been produced; which mitigates the lack of security fence; this question can be subsequently be graded as “Green” / If there is no security fence , answer the following mitigation question below					FGSR Note: / H&S - Imp Notice / (also part of handover check) / DTE sites who host Cadets / Reserves / Establishments with MQ in fence line (public access)
15.3.3			2.2.8-2 / Para 9 d / UK / LPG COP 1 Para 2.6.1			Compound security. 1.8m fence- Mitigation / A specific Risk Assessment, which has been updated within the previous 12 months, has been produced to mitigate the increased risk by having no security fence / If the specific Risk Assessment mitigates the justification of no security fence by other mechanisms of control; subsequent assessments can be assessed as “Green”					FGSR Note: / H&S - Imp Notice / (also part of handover check)
15.3.4			2.2.8-2 / Para 9d (note) / UK / LPG COP 1 Para 2.6.1 / (Para 2.6.3)			For LPG compounds without security fence / Access to Valves and fittings on the LPG tank (other than Px relief valve) shall be denied e.g. Locked covers fitted.					FGSR Note: / H&S - Imp Notice
15.3.5			2.2.8-2 / Para 9b / UK / LPG COP 1 Para 2.6.1			Compound security. 2 x outward opening gates. Not be self-locking, easily opening from the inside.					FGSR Note: / H&S - Imp Notice / Evidence of Compounds fitted with padlocks – main entrance unlocked, rear escape locked result in Immediate PN?
15.3.6			2.2.8-2 / Para 9c / UK / LPG COP 1 Para 2.6.1 / (Para 2.6.3)			Compound security. Distance from storage vessel to fence 1.5m (in attended 24/7 public areas)					FGSR Note: / H&S - Imp Notice
15.3.7			2.2.8-2 / Para 9d / UK / LPG COP 1 Para 2.6.1 / Para 2.6.5			Compound security. Distance from storage vessel to fence in unsecure (remote / unattended sites). 3.0m					(also part of handover check)
15.3.8			2.2.8-1 / Para 4 / UK / LPG COP 1 Para 3.1.5.9			LPG storage vessels should be properly installed on firm foundations & supported on concrete, masonry or structural steel supports. These supports should be so constructed or protected to ensure their load bearing capacity is maintained for same period as fire resistance for vessel. Recorded.					(also part of handover check)
15.3.9			2.2.8-1 / Para 5 / UKLPG / COP1 Para 2.5.1.1			Ground beneath vessel to be concrete or compacted & arranged to prevent pooling of spilled product. (Does not have to be the whole of the surface areas of the installation- recommend stone chippings out to end of separation distance)					(also part of handover check)
15.3.10			2.2.8-4 / Para 12b / UK / LPG COP 1 Para 2.6.4			Storage Vessel protection / vehicles – appropriate security from vehicle impact (Bollards, Armco Barrier)					FGSR Note: / H&S - Imp Notice / (also part of handover check)
15.3.11			2.2.8-6 / Para 6 / UK / LPG COP 1 Para 3.1.5.4			LPG vessels >2.2. Tonnes (or where piers are used as part of vessel support) / Vessel to be supported at one end only. Secured end where principal liquid & vapour lines are attached.
15.3.12			2.2.8-6 / Para 7 / UK / LPG COP 1 Para 3.1.4			LPG Storage Vessel shall be provided with visible, legible, & indelible markings: / Px vessel design code / Manuf name / Vessel Serial No / Max / Min design Px (bar) / Max / Min operating Temp / Vessel Date of Manuf / Water capacity in Litres / Date of test, px applied, inspection authorities identification / Provision for subsequent test marking

15.4 FIRE, HEALTH AND SAFETY					GRADING
					G	R	N/A	Remarks
Ref
15.4.1	2.2.6-5 / Table 1 / UK / LPG COP Table 8				Fire fighting extinguishers (combination of 9 kg dry powder, 9L water, 19 mm hose dependant on tank capacity- as well as fire fighting water supply). / <2200L / 19 mm and 2 x9 kg dry powder, / or / 4 x9 kg dry powder, / or / 2 x 9 kg dry powder and 2 x 9L water. / >2200L / 19 mm and 2 x9 kg dry powder					FGSR Note: / H&S - Imp Notice / (also part of handover check)
15.4.2	JSP 317				An installation specific fire plan is to be available at the installation. / It should include details of : / Fire detection and alarm systems / Water and other chemical fire fighting agents / Fire fighting equipment / Emergency shut down procedures / Emergency evacuation procedures & assembly points / Staff fire training / Duties of persons nominated in the plan / Arrangements for testing and updating the plan					Only required if operators reguarly access site as part of work activity – e.g DFRMO – Fire training rigs, Dog compounds- waste incinerators . / If not accessd by operators: then ensure at section 1 (1.3.1) has included this compound
15.4.3	2.2.6-7 / Para 34-36				Are fire posters and emergency evacuation posters available, in good condition and up-to-date? Located at all entry points.
15.4.4	2.2.8- / Annex A Table 1 Note				Smoking. No smoking is permitted within 3 m of the storage facility. Signage.
15.4.5	2.2.6-1 / Para 3h				All combustible material removed from LPG compound / Hazardous areas. / Chemical Weed Killers (e.g. sodium chlorate oxidising agent Prohibited) / Grass cutting within LPG Hazardous area under permit to Work					FGSR Note: / H&S - Imp Notice / KPI
15.4.6	2.2.6-1 / Para 3c / 2.2.8-4 / 12h				Areas outside the LPG Hazardous area should be kept free from a build-up of combustible materials (e.g. grass cuttings, leaves) / Weeds long grass deciduous shrubs / <2 Tonnes as Sep Dist ] / >2 Tonnes 6 m uklpg CoP 1, 2.3.1.10 & 2.6.2 / - recommend stone chippings out to end of separation distance)					FGSR Note: / H&S - Imp Notice / KPI / (also part of handover check)
15.4.7	2.2.6-2 / Par 6				Only approved PPE compatible for use with LPG to be worn					KPI H
15.4.8	2-2.6-7 / Para 36 / 2.2.8-4 / Para 12f				Suppliers emergency notice on Storage Vessel (24 Hr emergency Tel No)
15.4.9	2-2.6-7 / Para 36				Each tank to be labelled with product e.g. / PROPANE / BUTANE
15.4.10	2.2.8-3 / Para 12e / 2.2.6-7 / Para 36 / Fig 2.2.6.1				Adequate signage including safety signs, warning notices, around the boundaries of the storage area. To be clearly visible. Between 1.5-1.7m off ground. / NO SMOKING] / NO NAKED LIGHTS / NO STORAGE OF OIL GREASE OR COMBUSTIBLE MATERIALS / AUTHORISED PERSONS ONLY / NO MOBILE PHONES / NO STEEL TIPPED SHOES BOOTS / Flammable Gas transport diamond / LIQUEFIED PETROLEUM GAS or LPG

15.5 ROAD TANKER DELIVERY (Process carried out by Contractor)					GRADING
					G	R	N/A	Remarks
Ref
15.5.1		2.2.3-1 / Para 12			Road tanker –safe unrestricted access/ egress					FGSR Note: / H&S - Imp Notice / (also part of handover check) / Regulation – Condition of Certification
15.5.2		2.2.3-1 / Para 15a			Road tanker delivery area – level ground / slight chamber to direct spillage away from tanker					(also part of handover check) / Regulation – Condition of Certification
15.5.3		2.2.3-1 / Para 15a			Tanker operator should have clear line of sight to see both delivery tanker & LPG storage vessel					(also part of handover check)
15.5.4		2.2.3-1 / Para 13 / UK LPG COP 1 Para 7.3.3.5			Road Tanker delivery area should be separated from other traffic movements / (specific lay by or road barriers to prevent pedestrian / vehicular movement whilst LPG delivery taking place)					(also part of handover check) / Regulation – Condition of Certification
15.5.5		2.2.3-1 / Para 14 / UK LPG COP 1 Para 7.3.3.9			Road Tanker drive- away protection / prevention devices (signage) to be in place. Demonstrated either by:- / Contractor – designed vehicle. / Or- signage at delivery point / To ensure hazard cannot occur if the vehicle is moved before hose is disconnected					(also part of handover check)

15.6 LPG ISSUE / DISPENSE POINT (if applicable)					GRADING
					G	R	N/A	Remarks
Ref
15.6.1		Blue Book / Table 7.2.2			Bulk LPG Facility with Dispenser – / Buildings, boundary or fixed point of ignition 4m unoccupied Bldgs / 6m occupied Bldgs; / 9m accommodation blocks / From dispenser point
15.6.2		Blue Book 7.6.3			Pipework isolation to & from dispenser
15.6.3		Blue Book 7.6.4			Dispenser operated via deadmans button
15.6.4		Blue Book 7.6.4			Dispenser hose assy fitted with safe break connection
15.6.5		Blue Book 7.6.4			Dispenser Hose to BS1762 Spec (Lifed)
15.6.6		Blue Book 7.6.4			Dispenser fitted with sufficient valve for safe isolation testing & maintenance, with suitable sized return to Tank vessel for dispenser testing
15.6.7		Blue Book 7.6.4			Dispenser assy to be protected against vehicular damage (bollards Armco)
15.6.8		Blue Book 7.6.4			Operators of dispense points to be suitably trained / authorised (CofC)

Feedback

The FGSR are committed to continual development of the Assurance Assessment. Please use the box below to submit any comments, good or bad, and any suggestions or recommendations you may have and we will endeavour to continually improve the fuel safety assurance process.

Comments: