## Title sheet and version control
Discharge coefficient calculator
August 2018
DOCUMENT PROPERTIES
Organisation |  | Education & Skills Funding Agency
Name of Document |  | Discharge coefficient calculator
For use in conjunction with BB101 and the ESFA output specification to estimate the discharge coefficient of windows and natural ventilators for ventilation calculations.
Contents |  | Discharge coefficient calculator for windows and similar natural ventilation openings.
DOCUMENT VERSION CONTROL
Version | Comments and Amendments (details to be included where relevant) |  | Author/ Reviewer | Date | Approved by | Date approved
1 | Version for ESFA publication of BB101 2018 |  | Richard Daniels | 2018-08-09 | Crawford Wright | 2018-08-09
Notes on use of calculator
This excel spreadsheet calculator can be used to calculate the discharge coefficient Cd which is needed to estimate the effective area of ventilation opening areas. See Section 8.3 of BB101 and Section 11.3 of ESFA Output Specification Annex 2F on Ventilation opening areas. The calculator should only be used in the absence of emprical test results from manufacturers.
Acknowledgements
This spreadsheet tool was developed by Dr Benjamin Jones of Nottingham University.

## Cd Calculator
WINDOW DISCHARGE COEFFICIENT CALCULATOR |  |  | Data Table | [5 empty] | INSTRUCTIONS
Window width, w | 1 | m |  | b/h<0.5 | 0.5≤b/h≤1.0 | 1.0≤b/h≤2.0 | b/h≥2.0 | 1 | Use to diagram (right) to define the height, width, and opening angle of your window.
Window height, h | 1 | m | Gradient, M | 0.060476 | 0.047835 | 0.040464 | 0.038142 | 2 | Enter the lengths and angle into the calculator using the yellow boxes.
Opening angle, α | 10 | ⁰ | Coefficient, Cdmax | 0.61234 | 0.58861 | 0.5625 | 0.54826 | 3 | For sash windows, set α=90⁰.
Length ratio, b/h | 1 | -
Gradient, M | 0.040464 | -
Maximum Discharge Coefficient, Cdmax | 0.5625 | -
Stroke length, d | 0.17431 | m | [5 empty] | 4 | Use an appropriate area and a discharge coefficient, where required, in your models.
Orifice Discharge Coefficient, Cd0 | 0.62 | -
Equivalent area, Aeq | 0.30192 | m2 | [6 empty] | MODEL CAVEATS
Effective area, Aeff | 0.18719 | m2 | [5 empty] | 1 | This is a general model for hinged windows.
Free area, Afree | 1 | m2 | [5 empty] | 2 | The model does not use academic data and only gives an indication of appropriate values.
Discharge coefficient, Cd | 0.18719 | - | [5 empty] | 3 | All values are used at the users own risk.
[8 empty] | 4 | The model assumes the wind is normal to a wall in the horizontal and vertical planes.
[8 empty] | 5 | The model does not account for any type of reveal.
[8 empty] | 6 | When α<10⁰ the Aeff (and Cd, therefore) is extrapolated and so is not based on empirical data.
[8 empty] | 7 | When α<10⁰ the Aeff (and Cd, therefore) may not be constant when pressure differences
across the window are small.