## Specified generators: air dispersion modelling example short term statistical analysis
The applicant applies for an environmental permit to operate:
- an aggregated diesel specified generator site with a capacity of 40 MWth
- any time of the year for up to a maximum of 400 hours per year
Operations are expected to last up to 4 hours when needed.
Therefore, the operating envelope is all 8760 hours in the year. There are 400 operational hours within the operating envelope.
Dispersion modelling over the full year shows that the Predicted Environmental Concentration (PEC) exceeds the hourly mean limit value of 200mg/m3 for 300 hours at a sensitive receptor over the worst modelled meteorological year.
This gives:
- 400 operational hours - the sample size denoted by 'N'
- an 8760 hour operating envelope - the population size denoted by 'M'
- 300 exceedance hours - or the number of failures in the population denoted by 'e'
- 8460 non-exceedance hours - the number of successes in the population denoted by 'K', where K = M - e = 8760 - 300 = 8460
The probability of randomly selecting 19 or more exceedance hours (failures) in 400 sample trials, is the same as selecting at most 'N' minus 19 non-exceedance hours (successes) in 400 sample trials (N - 19 = 400 - 19 = 381). So you can calculate the probability of an exceedance, ‘P’ by using the cumulative hypergeometric distribution.

P equals the sum as i goes from 0 to (N minus 19) of K choose i times (M minus K) choose (N minus i) divide by M choose N, where P is cumulative hypergeometric probability of an exceedance, i is the index of summation, K is the number of non-exceedance hours, M is the number of hours in the operating envelope, and N is the number of operational hours.
Based on these data the cumulative hypergeometric distribution is 9.3%. As the continuous operations can be up to 4 hours, you multiply this probability by 2.5, giving a probability of exceedance of 23.25%. This indicates there is potential for an exceedance of the hourly standard.

The cumulative hypergeometric distribution calculates the probability to be less than 1.8% when there are 330 operational hours. Again multiplying this by the 2.5 factor gives a probability of 4.6%, indicating short term exceedances are unlikely.
Therefore we would propose to permit the generator and restrict the operational hours to 330 hours per year.