## Table 1
Generic risk assessment for standard rules set number SR2010 No2 v3.0
Standard Facility: |  |  |  | Water discharge activity: cooling water and heat exchangers
Location: |  |  |  | Applies to all potential locations (but see below for environmentally sensitive sites)
Risk assessment carried out by: |  |  |  | Environment Agency
Date: |  |  |  | 2013-05-31
The scope of the permit and associated rules is defined by the following risk criteria:
Parameter 1 | Permitted activities - the discharge of water from heating or cooling use, where the only change is the temperature.
Parameter 2 | Temperature change between inlet and outlet must be less than 8 degrees Celsius
Parameter 3 | The discharge must be to the same water body from which the water was abstracted, located to ensure maximum dilution in the receiving water and not within 200 metres of another cooling or heating discharge.
Parameter 4 | The temperature of the discharge at the outlet must not exceed twenty five degrees Celsius and the volume of the discharge must be less than 1000 cubic metres per day.
Parameter 5 | The total daily volume of the discharge shall not exceed 25% of the total daily flow in the receiving water body
Parameter 6 | The discharge shall not be made in ponds or lakes or freshwater within 500 metres upstream from the nearest boundary of a designated shellfish water, European Site, Ramsar site, Site of Special Scientific Interest (SSSI), Local Nature Reserve or any body of water identified as containing a Protected Species or within 100 metres from a Local Wildlife site
Abbreviations: SR - Standard Rule | SR - Standard Rule
WFD - Water Framework Directive
Data and information |  |  |  | Judgement |  |  |  | Action (by permitting)
Receptor | Source | Harm | Pathway | Probability of exposure | Conseque nce | Magnitude of risk | Justification for magnitude | Risk management | Residual risk
What is at risk? What do I wish to protect? | What is the agent or process with potential to cause harm? | What are the harmful consequences if things go wrong? | How might the receptor come into contact with the source? | How likely is this contact? | How severe will the conseque nces be if this occurs? | What is the overall magnitude of the risk? | On what did I base my judgement? | How can I best manage the risk to reduce the magnitude? | What is the magnitude of the risk after management? (This residual risk will be controlled by Compliance Assessment).
Local human population | Releases of microbiological pathogens (e.g. Legionella) | Harm to human health - respiratory irritation and illness. | Air transport then inhalation. | Low | Medium | Medium | Legionella can grow in water in heating and cooling systems. If present in the discharge they could be present in aerosol around the outlet. | SR (permitted activities) - discharge only of cooling/heating water, not including water recirculated within the system (i.e. closed circuit cooling/heating system). Risk of build up of Legionella very low. | Very Low
Local human population | Anti-fouling chemicals | Harm to human health - ingestion while | Ingestion while bathin, downstream abstraction for potable use. | Low | Medium | Medium | Systems may be treated from time to time to control biological fouling of pipes. | SR (permitted activities) - "emissions of substances not controlled by am emission limit" rules prevent dishcharge of any chemicals at concentrations that could cause pollution | Low
Local human population | Ingress of process chemicals into cooling water flow | Harm to human health - water contact | Ingestion while bathin, downstream abstraction for potable use. | Low | Medium | Medium | History of pollution incidents from this cause. | SR (permitted activities) - limited to situations where closed circuit cooling systems are uses. | Very Low
Plants and animals in the receiving water. | Heating of water. | Thermal shock; reduced dissolved oxygen levels, both producing stress to organisms and, in extreme cases, death. | Direct contact with water heated by the discharge. | Medium | Medium | Medium | Well known effects of thermal discharges producing excessive heating of the receiving water. | SR (permitted activities) - the temperature difference between the water at the inlet and outlet must be less than eight degrees Celsius, discharge is as far as is reasonably practicable located to maximise rapid dillution in the receiving water. SR - discharges must not be made directly to or within 500 or 100 metres up stream of specified nature conservation sites and protected species that could be affected. These precautions will ensure that temperature changes do not exceed WFD recommended levels. | Low
Plants and animals in the receiving water. | Anti-fouling chemcials | Harm to plant or animal health - water contact. | Direct contact with water chemicals in the discharge. | Medium | Medium | Medium | Water in recirculating systems must be treated to control biological fouling of pipes. | SR (permitted activities) - "emission os substances not controlled by am emission limit" rules prevent discharge of any chemicals at concentrations that could casue pollution. | Low
Plants and animals in the receiving water. | Cooling of water. | Excessive cooling affects activity and growth of plants and animals in the water; in extreme cases, freezing of the water. | Direct contact with water cooled by the discharge. | Low | Low | Low | The use of heat pumps to draw heat from water for heating buildings cools the receiving water during winter when temperatures are at their lowest. This may produce excessive cooling and even ice in the receiving water, particularly in city centres where many such uses may be concentrated. | This is only likely to be a problem in a limited number of locations, if any. In view of the environmental benefits of reducing use of fossil fuels for heating the only restrictions proposed are a limit ont he temperature change between inlet and outlet of 8 degrees and a minimum distance of 200 metres from any other cooling or heating discharge. | Low
Plants and animals in the receiving water. | Ingress of process chemicals into cooling water flow | Harm to plant or animal health - water contact. | Direct contact with water chemicals in the discharge. | Medium | Medium | Medium | History of pollution incidents from this source. | SR (permitted activities) - limited to situations where closed circuit cooling systems are used. SR - activities will be managed and operated in accordance with a management system (will include inspection and maintenance). | Very Low