## PES Calculation
Scheme details: Please enter data in green cells
Total power capacity |  | MW
Scheme performance data: Please enter relevant data (from certificate) in green boxes
Total fuel input | 4 | MWh GCV
Total power output | 2 | MWh GCV
Qualifying heat output | 1 | MWh GCV
Fuel data: Please make selection of fuel type and % below in green boxes
Enter type and % of fuel on a GCV basis | Fuel Type | % (total should be 100%)
Primary fuel | S5 Other solid biomass including all wood not included under S4 and black and brown liquor. | 50%
Secondary fuel | G12 Biogas produced from anaerobic digestion, landfill, and sewage treatment | 40%
Tertiary fuel | G10 Natural gas, LPG, LNG and biomethane | 10%
| S | 100%
Grid connection: Please enter data below in green boxes
On-site electricity use | 100%
Is the scheme connected to the grid | Yes
Grid connection | 100-200kV
Power Efficiency (GCV) | = | 50%
Heat Efficiency (GCV) | = | 25%
Overall Efficiency (GCV) | = | 75%
PES | = | 46%

## Data (hidden)
Look-up data
COMMISSION DELEGATED REGULATION (EU) 2015/2402 of 12 October 2015 reviewing harmonised efficiency reference values for separate production of electricity and heat in application of Directive 2012/27/EU of the European Parliament and of the Council and repealing Commission Implementing Decision 2011/877/EU. http://eur-lex.europa.eu/legal-content/EN/TXT/PDF/?uri=CELEX:32015R2402&from=EN
Fuel Code | Fuel Type | Heat Ref values |  | Electricity Ref values | NCV/GCV
|  | Steam/HW | Direct EG |  | factor
S1 | S1 Hard coal including anthracite, bituminous coal, sub-bituminous coal, coke, semi-coke, pet coke | 88% | 80% | 44.2% | 0.95
S2 | S2 Lignite, lignite briquettes, shale oil | 86% | 78% | 41.8% | 0.95
S3 | S3 Peat, peat briquettes | 86% | 78% | 39% | 0.95
S4 | S4 Dry biomass including wood and other solid biomass including wood pellets and briquettes, dried woodchips, clean and dry waste wood, nut shells and olive and other stones | 86% | 78% | 37% | 0.94991
S5 | S5 Other solid biomass including all wood not included under S4 and black and brown liquor. | 80% | 72% | 30% | 0.94991
S6 | S6 Municipal and industrial waste (non-renewable) and renewable/ bio-degradable waste | 80% | 72% | 25% | 0.94991
L7 | L7 Heavy fuel oil, gas/diesel oil, other oil products | 85% | 81% | 44.2% | 0.94
L8 | L8 Bio-liquids including bio-methanol, bioethanol, bio-butanol, biodiesel and other bio-liquids | 85% | 81% | 44.2% | 0.94991
L9 | L9 Waste liquids including biodegradable and non-renewable waste (including tallow, fat and spent grain). | 75% | 72% | 29% | 0.94991
G10 | G10 Natural gas, LPG, LNG and biomethane | 92% | 82% | 53% | 0.9
G11 | G11 Refinery gases hydrogen and synthesis gas | 90% | 81% | 44.2% | 0.9009
G12 | G12 Biogas produced from anaerobic digestion, landfill, and sewage treatment | 80% | 62% | 42% | 0.9009
G13 | G13 Coke oven gas, blast furnace gas, mining gas, and other recovered gases (excluding refinery gas) | 80% | 72% | 35% | 0.9009
O14 | O14 Waste heat (including high temperature process exhaust gases, product from exothermic chemical reactions) | 92% | 0% | 30% | 0.95
None
COMMISSION DELEGATED REGULATION (EU) 2015/2402 of 12 October 2015 reviewing harmonised efficiency reference values for separate production of electricity and heat in application of Directive 2012/27/EU of the European Parliament and of the Council and rep
Catno | Grid Connection | Electricity exported to grid | Electricity consumed on site
1 | >345kV | 1 | 0.976
2 | 200-345kV | 0.972 | 0.963
3 | 100-200kV | 0.963 | 0.951
4 | 50-100kV | 0.952 | 0.936
5 | 12-50kV | 0.935 | 0.914
6 | 0.4-12kV | 0.918 | 0.891
7 | <0.4kV | 0.888 | 0.851
|  | % | %
Selected |  | 0% | 100%
3 | 100-200kV | 0.963 | 0.951
| Aggregate Grid CF |  | 0.951
Fuel Code | Fuel mix (based on user input) | GCV | NCV
S1 | S1 Hard coal including anthracite, bituminous coal, sub-bituminous coal, coke, semi-coke, pet coke | 0% | 0%
S2 | S2 Lignite, lignite briquettes, shale oil | 0% | 0%
S3 | S3 Peat, peat briquettes | 0% | 0%
S4 | S4 Dry biomass including wood and other solid biomass including wood pellets and briquettes, dried woodchips, clean and dry waste wood, nut shells and olive and other stones | 0% | 0%
S5 | S5 Other solid biomass including all wood not included under S4 and black and brown liquor. | 50% | 51.33%
S6 | S6 Municipal and industrial waste (non-renewable) and renewable/ bio-degradable waste | 0% | 0%
L7 | L7 Heavy fuel oil, gas/diesel oil, other oil products | 0% | 0%
L8 | L8 Bio-liquids including bio-methanol, bioethanol, bio-butanol, biodiesel and other bio-liquids | 0% | 0%
L9 | L9 Waste liquids including biodegradable and non-renewable waste (including tallow, fat and spent grain). | 0% | 0%
G10 | G10 Natural gas, LPG, LNG and biomethane | 10% | 9.726%
G11 | G11 Refinery gases hydrogen and synthesis gas | 0% | 0%
G12 | G12 Biogas produced from anaerobic digestion, landfill, and sewage treatment | 40% | 38.94%
G13 | G13 Coke oven gas, blast furnace gas, mining gas, and other recovered gases (excluding refinery gas) | 0% | 0%
O14 | O14 Waste heat (including high temperature process exhaust gases, product from exothermic chemical reactions) | 0% | 0%
| Weigted average reference heat efficiency (Net CV) |  | 81.17%
| Weighted average reference power efficiency (Net CV) |  | 36.91%
| Avg UK Temp Deg C |  | 10
| Temp corrected average reference power efficiency (Net CV) |  | 37.41%
| Temp and Grid Connection corrected average reference power efficiency (Net CV) |  | 35.58%
| NCV/GCV |  | 0.92532