MOD FORM 2210

CONDUCTING & ANTI-STATIC FLOORS RECORD SHEET

| Site: | Building: |
| --- | --- |
| Floor Type |
|  | Conducting |
|  | Antistatic |
| Visual Inspection |
|  | (1) Visually inspect the floor for signs of wear, damage or contamination and identify affected areas |
|  | (2) Visually confirm the integrity of the equipotential bonding system including that it is routed to the common earth star point (MET) only (no supplementary connections to LPS) |
|  | (3) HAPTM is working correctly and positioned directly over floor |
|  | (4) Floor is earthed to the equipotential bonding (EPB) strip at a minimum of 2 places |
|  | (5) Visually check integrity of electrical bonding of benches, floors, chairs, trolleys, mats, workstations, separately grounded equipment and any other equipment that grounds an operator permanently or temporarily |
|  | (6) Socket outlets are RCD protected |
| Equipotential Bonding/Static Discharge System |
| Visually inspect the Static Discharge System and ensure it is: |
|  | (1) As low as possible on the walls (no higher than 500mm from ground level) |
|  | (2) Connected to the main earthing terminal with the electrical incomer sheath and other earth systems via the shortest possible length |
|  | (3) Not connected directly to the LPS, other than at the MET |
|  | (4) Run in as straight a line as possible with minimal bends and corners |
|  | (5) Where it is run over an opening, no bonding connections are made to it above the opening |
|  | (6) Securely fitted with tight connections |
|  | (7) Free of deterioration, corrosion and damage |
| Static Discharge System Test |
|  | (1) Static Discharge Continuity Test Results (Ω) |
|  | (2) Earth electrode test |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Enter the following symbols against the test as appropriate:

(	To indicate an inspection has been carried out and the result is satisfactory

N/A	To indicate an inspection is not applicable

C1, C2 or C3 – To indicate observations found

| Site: | Building: |
| --- | --- |
| Floor Diagram and Test Results (kΩ) |

| Test Instrument details |
| --- |
| Manufacturer: | Model: | Serial No: | Calibration Date: |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

REMEDIAL ACTIONS ARISING FROM CONDUCTIVE/ANTI-STATIC FLOOR TEST RESULTS

| Site: | Building: |
| --- | --- |
| OBSERVATION | CLASSIFICATION CODE | Recommended remedial action | Date of Action Complete |

Inspected by:

Name (Capitals) ………………………………………………..

Signature ……………………………………………................

Date ……………………………………………........................

Classification Codes

Each observation relating to a concern about the safety of the installation shall be attributed an appropriate Classification Code selected from the standard codes C1, C2 and C3 as follows:

Code C1	‘Danger present’ Risk of injury. Immediate remedial action required

Code C2	‘Potentially dangerous’ Urgent remedial action required

Code C3	‘Improvement recommended’