## Table 1
Generic risk assessment for standard rules set number SR2010No3 v3.0
Activity type: |  |  |  | Water discharge activity: secondary treated sewage discharges with flow limit between 5 and 20 m3/day
Location: |  |  |  | Applies to all potential locations
Location of environmentally sensitive sites (kilometre / m): |  |  |  | Greater than 1kilometre or 100 metres (see below)
Risk assessment carried out by: |  |  |  | Environment Agency
Date: |  |  |  | 2013-05-31
The scope of the standard permit is defined by the following risk criteria:
Parameter 1 | Permitted activities - the discharge is solely secondary treated domestic sewage containing no trade effluent
Parameter 2 | The total daily flow of the discharge calculated by the method specified in "Flows and Loads 3" shall be greater than 5 m3/d but not greater than 20 m3/d
Parameter 3 | The discharge shall only be made to a watercourse that normally contains water throughout the year
Parameter 4 | The sewage must have received secondary treatment at a treatment plant designed and constructed to meet the requirements of BS 12566 and sized in accordance with “Flows and Loads 3”
Parameter 5 | The discharge cannot reasonably, at the time it is first made, be made to an existing foul sewer
Parameter 6 | The discharge shall not be made into ponds or lakes or freshwater within 1 kilometre upstream from the nearest boundary of an identified bathing water, a designated shellfish water, European Site, Ramsar site, Site of Special Scientific Interest (SSSI), Local Nature Reserve or any body of water identified as containing a Protected Species or within 100 metres from a Local Wildlife site. Only sites that are water-based and linked to the receiving water downstream of the discharge point are included in the rule.
Abbreviations: SR - Standard rule
"Flows and loads 3" Flows and Loads 3 - Sizing Criteria, Treatment Capacity for Small Wastewater Treatment Systems (Package Plants)
Data and information |  |  |  | Judgement |  |  |  | Action (by permitting)
Receptor | Source | Harm | Pathway | Probability of exposure | Conseque nce | Magnitude of risk | Justification for magnitude | Risk management | Residual risk
What is at risk? What do I wish to protect? | What is the agent or process with potential to cause harm? | What are the harmful consequences if things go wrong? | How might the receptor come into contact with the source? | How likely is this contact? | How severe will the conseque nces be if this occurs? | What is the overall magnitude of the risk? | On what did I base my judgement? | How can I best manage the risk to reduce the magnitude? | What is the magnitude of the risk after management? (This residual risk will be controlled by Compliance Assessment).
Local human population | odour | Unpleasant smell around plant | Living or visiting near a malfunctioning plant | Low | Low | Low | Serious smell only likely from modern plant of adequate capacity when it is seriously malfunctioning | SR - activities shall be managed and operated in accordance with a management system (will include inspection and maintenance). | Very low
| discharge of visible solids | Visible pollution of receiving water | malfunctioning plant discharge to water | Low | Low | Low | Excessive solids only likely from modern plant when it is seriously malfunctioning
| bacteria and viruses | illness | swimming in water close downstream or consuming shellfish from close downstream | Medium | High | High | swimming or eating uncooked shellfish from sewage affected water is a potential health risk. Sewage can cause Directive failure | SR - the discharge must not be made within 1kilometre upstream from an identified bathing water or a designated shellfish water. | Low
Chemical and biological quality of the receiving water | organic matter | Removes oxygen from water, can become completely anoxic. Can damage plants and animals | In the discharge to water | Medium | Medium | Medium | Deoxygenation of water is one of the most severe potential effects of excessive organic discharge load | SR (permitted activities) - • Prior to the discharge, the sewage must have received secondary treatment at a treatment plant designed and constructed to meet the requirements of BS 12566 (or equivalent); or for discharges over 9m3/day an equivalent standard, and sized in accordance with "Flows and Loads 3" | Low
| suspended solids | Excess blankets bed of water. Can damage plants and animals | In the discharge to water | Low | Medium | Medium | Suspended solids from treated sewage is rarely sufficient to cause a problem unless the plant malfunctions | As above and SR - activities shall be managed and operated in accordance with a management system (will include inspection and maintenance). | Low
| ammonia | Removes oxygen from water, can be directly toxic. Can damage plants and animals | In the discharge to water | Low | Medium | Medium | Ammonia from treated sewage is rarely sufficient to cause a problem unless the plant malfunctions | As above. Design according to Flows and Loads 3 should ensure sufficient nitrification (Oxidation to Nitrate and Nitrite) is normally achieved | Low
| toxic substances | Directly toxic to plants and animals | In the discharge to water | Low | Medium | Medium | Domestic sewage does not normally contain significant concentrations of toxic substances | SR (permitted activities) - the sewage must be solely domestic in origin | Low
| phosphorus | Excess stimulates plant growth. Can change plant ecology or promote algal blooms | In the discharge to water | Low | Low | Low | All sewage contains phosphorus, but small treated discharges rarely have any appreciable effect on their own | No action possible or needed as load of phosphorus from the permitted activity will be small. | Very low
Protected sites/species | pollutants and nutrients in the discharge | Adversely affect the plants and animals of interest in the site | In the discharge to water | Low | Medium | Medium | Substances in treated sewage will alter the water chemistry to some extent and this may be large enough to adversely affect a conservation site or species that relies on surface water | SR - discharges shall not be made within 1kilometre or 100 metres upstream from specified nature conservation sites and protected species that could be affected. Outside of that distance the effect of the discharge will not be detectable and therefore there is no potential for detrimental impact | Low