## PES Calculation
Scheme details: Please enter data in green cells
Total power capacity |  | MW
Scheme performance data: Please enter relevant data (from certificate) in green boxes
Total fuel input |  | MWh
Total power output |  | MWh
Qualifying heat output |  | MWh
Fuel data: Please make selection of fuel type and % below in green boxes
Enter number of fules | 3
Enter type and % of fuel | Fuel Type | % (total should be 100%)
Primary fuel | Solid biomass/waste
Secondary fuel | Biogas
Tertiary fuel | Natural Gas
Grid connection: Please enter data below in green boxes
On-site electricity use | 100%
Is the scheme connected to the grid | Yes
Grid connection | 100-200kV
Heat Efficiency | = | #DIV/0!
Overall Efficiency | = | #DIV/0!
PES | = | #DIV/0!

## Data (hidden)
Look-up data
Electricity Efficiency Reference Values (Annexes I and II of 2011/877/EC)
Fuel Type | Heat Ref values |  | Electricity Ref values | Net / Gross conversion
| Steam/HW | Direct EG |  | factor
Natural Gas | 90% | 82% | 52.5% | 1.109
Fuel Oil | 89% | 81% | 44.2% | 1.06
Coal/Coke | 88% | 80% | 44.2% | 1.05
Refinery Gas | 89% | 81% | 44.2% | 1.109
Low CV/waste gases | 80% | 72% | 35% | 1.109
Wood fuels | 86% | 78% | 33% | 1.077
Agricultural biomass | 80% | 72% | 25% | 1.077
Biodegradable (municipal waste) | 80% | 72% | 25% | 1.077
Non-renewable (municipal and industrial) waste | 80% | 72% | 25% | 1.077
Oil shale | 86% | 78% | 39%
Solid biomass/waste | 80% | 72% | 25% | 1.05
Liquid biofuels | 89% | 81% | 44.2% | 1.077
Liquid bio waste/waste | 80% | 72% | 25% | 1.077
Biogas | 70% | 62% | 42% | 1.077
Lignite | 86% | 78% | 41.8% | 1.05
Peat | 86% | 78% | 39% | 1.05
Correction factors for avoided grid losses (Annex IV of 2011/877/EC)
Grid Connection | Electricity exported to grid | Electricity consumed on site
>200kV | 1 | 0.985
100-200kV | 0.985 | 0.965
50-100kV | 0.965 | 0.945
0.4-50kV | 0.945 | 0.925
<0.4kV | 0.925 | 0.86
Fuel mix (based on user input)
Natural Gas | 0%
Fuel Oil | 0%
Coal/Coke | 0%
Refinery Gas | 0%
Low CV/waste gases | 0%
Wood fuels | 0%
Agricultural biomass | 0%
Biodegradable (municipal waste) | 0%
Non-renewable (municipal and industrial) waste | 0%
Oil shale | 0%
Solid biomass/waste | 0%
Liquid biofuels | 0%
Liquid bio waste/waste | 0%
Biogas | 0%
Lignite | 0%
Peat | 0%
Weigted average heat efficiency (Net CV) | 0%
Weighted average power efficiency (Net CV) | 0%