## Title and version control
ICT equipment heat gains calculator
August 2018
DOCUMENT PROPERTIES
Organisation |  | Education & Skills Funding Agency
Name of Document |  | ICT equipment heat gains calculator
For use in conjunction with BB101 and the ESFA output specification to estimate heat loads from ICT equipment for heat loss calculations.
Contents |  | ESFA scenarios can be used to estimate heat loads in common teaching spaces. The information in the remainder of the spreadsheet is a review of all the available information at January 2017.
DOCUMENT VERSION CONTROL
Version | Comments and Amendments (details to be included where relevant) |  | Author/ Reviewer | Date | Approved by | Date approved
1 | Version for ESFA publication of BB101 2018 |  | Richard Daniels | 2018-08-09 | Crawford Wright | 2018-08-09
Notes on use of calculator
The excel spreadsheet calculator at ESFA scenarios can be used to calculate the ICT equipment heat load in a space. It is intended to supplement BB101 2018 and the ESFA Ouput Specification. Designers should be aware that the data in the three information tables resulted from a review carried out in 2017. As equipment and the way it is used is continually changing designers should update this information as necessary.
Acknowledgements
This spreadsheet tool was developed by Dr Tim Taylor of Atkins Global.

## ICT Energy Efficiency
Technology Trends
Johnston et al. (2011) "Trends in Office Internal Gains and the Impact on Space Heating and Cooling"
Identifies future technology trends with potential to influence internal gains in the context of offices.
Trends of relevance to schools include:
Ubiquitous computing: simply defined as "computers everywhere", associated with 4 key drivers
1. Cloud computing: processing power moves away from desktop PCs to a server network (either public or private cloud)
2. Mobile computing: increased usage of mobile devices (netbooks, tablets, smartphones) with most processing requirements undertaken in the cloud
3. Surface computing: interactive sceens are becoming the norm - whilst individual devices are getting more energy efficient, there is trend towards larger (and multiple) monitors
4. Pervasive sensor networks: better monitoring of buildings through the "Internet of Things" and intelligent integration with Building Management Systems
Solid State Lighting: high-efficiency LED luminaires are now available on the market
Together, these trends could drive power consumption either towards an "energy-conscious scenario" or "techno-explosion" scenario as described in the paper:
Energy conscious scenario: massive reductions in demand through
1. Developments in energy efficiency: recent developments include solid state drives and LCD monitors with LED backlights
2. Cloud computing and virtual desktops: processing power moved to the cloud
3. Advances in mobile technology: mobile devices are inherently energy efficient in order to conserve battery power
4. Paperless office: reduces electrical energy demand from printers and copiers
Techno-explosion scenario: large increases in demand through
1. Surface computing: larger and multiple interactive screens (there has been a parallel trend of devices getting larger alongside increases in efficiency, resulting in a zero net energy benefit)
2. Consumer mentality: as equipment costs decrease consumers use this spare capital to purchase more (Jevons' paradox)

## Internal Gains Data
CIBSE Guide A (2015 edition) |  |  |  |  | Summary
6.5.2 "It is well documented that nameplate power overstates the actual power and consequent heat gain."
CIBSE Guide A (2015)
Average power consumption (W)
[5 empty] | Item | Min. | Max. | Avg. | n
[5 empty] | Desktop PC | 48 | 97 | 68.8 | 5
[5 empty] | Laptop computer | 12 | 36 | 26.6667 | 6
[5 empty] | Flat panel monitor | 19 | 90 | 38.1667 | 6
Menezes et al. (2013)
Average power consumption (W)
[5 empty] | Item | Min. | Max. | Avg. | n
[5 empty] | Desktop PC | 64.1 | 168.6 | 116.35 | 2
[5 empty] | Laptop computer | 17.9 | 30.9 | 23.0333 | 3
[5 empty] | Flat panel monitor | 23.2 | 35.7 | 27.1 | 3
Menezes et al. (2013) "Benchmarking small power energy consumption in UK office buildings: a review of data published in CIBSE Guide F"
2013 ESFA ICT advisers figures
Item | Active (Watts) | Passive (Watts) | Generic Value (Watts)
Desktop Computer | 105 | 75 | 47
Apple iMac 21" | 113 | n/a | 53 | Reduce to 53 Active from ARUP report
Laptop | 35 | 5 | 15 | 15 from CIBSE full operation
Wireless Access Point | 12 | 10 | 12
Data Projector | 250 | n/a | 210
Interactive Whiteboard | 200 | n/a | 200
Speakers (2) | 35 | 5 | 9
IP Telephone | 4 | 5 | 4
Network Printer | 567 | 55 | 160

## Diversity
CIBSE Guide A (2015 edition)
6.5.3 "The actual peak internal heat gain for all office equipment in a single common area is less than the sum of the individual continuous gains due to diversity of use… it is a factor that accounts for a percentage of equipment being idle or turned off."
Wilkins & Hosni (2011) Plug load design factors - ASHRAE Journal article
Following diversity factors recommended for office equipment:

## ESFA Scenarios
EFA ICT usage scenarios
Note that the minimum and maximum values stated in the tables refer to the lowest and highest average power consumption for that device reported in the references consulted.
Data sources
1. CIBSE Guide A (2015 edition)
2. Menezes et al. (2013)
3. EFA Advisers ICT Figures
4. Johnston et al. (2011)
These data sources are referenced as the basis for the heat gain calculations given below for the EFA ICT usage scenarios.
Standard teaching space with 1:1 pupil:laptop
All pupils assumed to use a laptop during class, teacher also uses a laptop as well as data projector with speakers.
Room includes one wireless access point.
|  | Gain per item (W) |  |  | Diversity (%) | Total per item (W) |  |  | Data source
Device | No. items | Min. | Max. | Typ. |  | Min. | Max. | Typ. | Min. | Max. | Typ. | Notes
Student laptop | 30 | 12 | 36 | 18 | 0.75 | 270 | 810 | 405 | 1 | 1 | 2 | Typical value based on laptop with 2.6GHz Intel Core i5 processors
Staff laptop | 1 | 12 | 36 | 18 | 0.75 | 9 | 27 | 13.5 | 1 | 1 | 2 | Typical value based on laptop with 2.6GHz Intel Core i5 processors
Data projector | 1 | 250 | 250 | 250 | 0.5 | 125 | 125 | 125 | 3 | 3 | 3 | Based on peak power consumption, diversity factor of 0.5 assumed
Speakers | 1 | 9 | 9 | 9 | 0.5 | 4.5 | 4.5 | 4.5 | 3 | 3 | 3 | Diversity factor of 0.5 assumed
Wireless Access Point | 1 | 12 | 12 | 12 | 1 | 12 | 12 | 12 | 3 | 3 | 3 | Diversity factor of 1 assumed
[5 empty] | Room total ICT gain (W) | 420.5 | 978.5 | 560
[5 empty] | Room area | 55 | 55 | 55
[5 empty] | Room total ICT gain (W/m2) | 7.6455 | 17.7909 | 10.1818
Standard teaching space with 2:1 pupil:laptop
Half of pupils assumed to use a laptop during class, teacher also uses a laptop as well as data projector with speakers.
Room includes one wireless access point.
|  | Gain per item (W) |  |  | Diversity (%) | Total per item (W) |  |  | Data source
Device | No. items | Min. | Max. | Typ. |  | Min. | Max. | Typ. | Min. | Max. | Typ. | Notes
Student laptop | 15 | 12 | 36 | 18 | 0.75 | 135 | 405 | 202.5 | 1 | 1 | 2 | Typical value based on laptop with 2.6GHz Intel Core i5 processors
Staff laptop | 1 | 12 | 36 | 18 | 0.75 | 9 | 27 | 13.5 | 1 | 1 | 2 | Typical value based on laptop with 2.6GHz Intel Core i5 processors
Data projector | 1 | 250 | 250 | 250 | 0.5 | 125 | 125 | 125 | 3 | 3 | 3 | Based on peak power consumption, diversity factor of 0.5 assumed
Speakers | 1 | 9 | 9 | 9 | 0.5 | 4.5 | 4.5 | 4.5 | 3 | 3 | 3 | Diversity factor of 0.5 assumed
Wireless Access Point | 1 | 12 | 12 | 12 | 1 | 12 | 12 | 12 | 3 | 3 | 3 | Diversity factor of 1 assumed
[5 empty] | Room total ICT gain (W) | 285.5 | 573.5 | 357.5
[5 empty] | Room area | 55 | 55 | 55
[5 empty] | Room total ICT gain (W/m2) | 5.1909 | 10.4273 | 6.5
Specialised IT teaching space
All pupils assumed to use desktop PC during class, teacher uses a laptop as well as data projector with speakers.
Room includes one wireless access point.
|  | Gain per item (W) |  |  | Diversity (%) | Total per item (W) |  |  | Data source
Device | No. items | Min. | Max. | Typ. |  | Min. | Max. | Typ. | Min. | Max. | Typ. | Notes
Student desktop PC | 30 | 48 | 169 | 64 | 0.75 | 1080 | 3802.5 | 1440 | 1 | 2 | 2 | Typical value based on 2.3Ghz Intel Core Duo processors desktop PC
Student monitor | 30 | 19 | 90 | 36 | 0.6 | 342 | 1620 | 648 | 1 | 1 | 1 | Typical value based on 22" monitor
Staff laptop | 1 | 12 | 36 | 18 | 0.75 | 9 | 27 | 13.5 | 1 | 1 | 2 | Typical value based on laptop with 2.6GHz Intel Core i5 processors
Data projector | 1 | 250 | 250 | 250 | 0.5 | 125 | 125 | 125 | 3 | 3 | 3 | Based on peak power consumption, diversity factor of 0.5 assumed
Speakers | 1 | 9 | 9 | 9 | 0.5 | 4.5 | 4.5 | 4.5 | 3 | 3 | 3 | Diversity factor of 0.5 assumed
Wireless Access Point | 1 | 12 | 12 | 12 | 1 | 12 | 12 | 12 | 3 | 3 | 3 | Diversity factor of 1 assumed
[5 empty] | Room total ICT gain (W) | 1572.5 | 5591 | 2243
[5 empty] | Room area | 83 | 83 | 83
[5 empty] | Room total ICT gain (W/m2) | 18.9458 | 67.3614 | 27.0241
Specialised teaching space (e.g. art, music, etc.) with 2:1 pupil:mac
Teaching space is provided with 16 Apple iMac 21" computers as well as a data projector with speakers.
Room includes one wireless access point.
|  | Gain per item (W) |  |  | Diversity (%) | Total per item (W) |  |  | Data source
Device | No. items | Min. | Max. | Typ. |  | Min. | Max. | Typ. | Min. | Max. | Typ. | Notes
Apple iMac 21" | 16 | 53 | 53 | 53 | 0.75 | 636 | 636 | 636 | 3 | 3 | 3 | Typical value based on 2.3Ghz Intel Core Duo processors desktop PC
Data projector | 1 | 250 | 250 | 250 | 0.5 | 125 | 125 | 125 | 3 | 3 | 3 | Based on peak power consumption, diversity factor of 0.5 assumed
Speakers | 1 | 9 | 9 | 9 | 0.5 | 4.5 | 4.5 | 4.5 | 3 | 3 | 3 | Diversity factor of 0.5 assumed
Wireless Access Point | 1 | 12 | 12 | 12 | 1 | 12 | 12 | 12 | 3 | 3 | 3 | Diversity factor of 1 assumed
[5 empty] | Room total ICT gain (W) | 777.5 | 777.5 | 777.5
[5 empty] | Room area | 83 | 83 | 83
[5 empty] | Room total ICT gain (W/m2) | 9.3675 | 9.3675 | 9.3675
Standard teaching space with 1:1 pupil:tablet
All pupils assumed to use a tablet device during class, teacher uses a laptop as well as data projector with speakers.
Room includes one wireless access point.
|  | Gain per item (W) |  |  | Diversity (%) | Total per item (W) |  |  | Data source
Device | No. items | Min. | Max. | Typ. |  | Min. | Max. | Typ. | Min. | Max. | Typ. | Notes
Student tablet | 30 | 2.5 | 5 | 5 | 0.75 | 56.25 | 112.5 | 112.5 | 4 | 4 | 4 | Typical value based on tablet with 5W heat output (maximum value given in reference)
Staff laptop | 1 | 12 | 36 | 18 | 0.75 | 9 | 27 | 13.5 | 1 | 1 | 2 | Typical value based on laptop with 2.6GHz Intel Core i5 processors
Data projector | 1 | 250 | 250 | 250 | 0.5 | 125 | 125 | 125 | 3 | 3 | 3 | Based on peak power consumption, diversity factor of 0.5 assumed
Speakers | 1 | 9 | 9 | 9 | 0.5 | 4.5 | 4.5 | 4.5 | 3 | 3 | 3 | Diversity factor of 0.5 assumed
Wireless Access Point | 1 | 12 | 12 | 12 | 1 | 12 | 12 | 12 | 3 | 3 | 3 | Diversity factor of 1 assumed
[5 empty] | Room total ICT gain (W) | 206.75 | 281 | 267.5
[5 empty] | Room area | 55 | 55 | 55
[5 empty] | Room total ICT gain (W/m2) | 3.7591 | 5.1091 | 4.8636