## Title and version control
Window and damper draught - line plume - calculator
March 2018
DOCUMENT PROPERTIES
Organisation |  | Education & Skills Funding Agency
Name of Document |  | Calculator for window and damper draught
for use in conjunction with BB101 and the ESFA Output Specification: Annex 2F
Contents |  | Calculator for window and damper draught - line plume - calculator
DOCUMENT VERSION CONTROL
Version | Comments and Amendments (details to be included where relevant) |  | Author/ Reviewer | Date | Approved by | Date approved
1 | Version published by ESFA with BB101 2018 |  | Richard Daniels | 2018-03-21 | Crawford Wright | 2018-03-21
Notes on use of calculator
The following excel spreadsheet shows how the temperature of an incoming stream of cold air through a high level window or damper into a warm room increases as the turbulent plume falls under gravity and entrains warm room air. It is to help in the assessment of the most appropriate openings for wintertime ventilation.
Acknowledgements
This spreadsheet tool was developed by Dr Shaun Fitzgerald of Breathing Buildings and the Department of Engineering at the University of Cambridge.
ESFA would also like to thank Prof Malcolm Cook (Loughborough University) and Prof Colm Caulfield (University of Cambridge) for their contributions on modelling.

## Calculator
Distance to reach fully turbulent flow | 0 | m | set this to be zero if you want to allow entrainment to start as soon as air enters the room - this is the most optimistic assumption possible for a window
Width of opening window/damper | 3 | m
Average temperature of classroom | 21 | C
Height from floor to top of opening window/damper | 2.7 | m
Vertical extent of opening high level window/damper | 0.5 | m
High level opening type | Top hung window
Number of occupants | 32
Minimum fresh air rate per person | 5 | l/s
This spreadsheet tool is based on standard plume theory from Turner (1973), Buoyancy Effects in Fluids. It also uses the concept of a virtual origin for plumes following the work of Kaye & Hunt. It shows how the temperature of an incoming stream of cold air through a high level window or damper into a warm room increases as the turbulent plume falls under gravity and entrains warm room air. The entrainment is just from one side of the line plume since the other side is against the window. When the temperature of the plume 1.4m from the floor (given by the light blue line for secondary schools) or 1.1m from the floor (given by the dark blue line for primary schools) is below the minimum acceptable level for schools (given by the red line) for any external temperature above 5C (denoted by the dotted black line), the system FAILS to meet the criterion for draughts as laid out in 2017 BB101, which is that the temperature needs to be within 5C of the ambient temperature for all external temperatures above 5C. When the temperature of the plume (blue lines) is above the minimum temperature (red line), the system PASSES the criterion for cold draughts.
The model assumes that the flow is fully turbulent the moment air enters the room. This is the most optimistic assumption with regards to the effectiveness of mixing. Note that the effects of gusts are also not accounted for. Finally, although entrainment is modelled only from one side of the plume, the reduced turbulence arising from the fact that the plume is constrained by a solid boundary is also not included. The modelling results therefore indicate an optimistic view of the mixing effectiveness and colder temperatures at the occupied level may be experienced.
The results should be interpreted as follows:
1) If the temperatures predicted show a FAIL then it is very likely that draughts will be a serious issue in your design and alternative solutions are recommended.
2) If the temperatures predicted show a MARGINAL PASS then anyone using this design should only do so with extreme caution as draughts may well still be a problem.
3) If the temperatures predicted show a CLEAR PASS then the designer can proceed, but note that the results do not guarantee draught free conditions at all times. If completely draught free conditions are desired under all weather conditions then alternative ventilation solutions should be pursued.
For more information please see www.breathingbuildings.com
Furthermore, if anyone wishes to obtain the full calculations in the spreadsheet please contact info@breathingbuildings.com
This spreadsheet tool is free for designers to use to help them in the assessment of the most appropriate openings for wintertime ventilation.
The entrainment coefficient for turbulent plumes is usually taken to be 0.102. However, following work undertaken by Prof Malcolm Cook (Loughborough University), Prof Paul Linden, David Parker and Prof Colm-cille Caulfied (University of Cambridge), and discussions with Dr Henry Burridge (Imperial College), Dr Connick (Breathing Buildings) and Dr Shaun Fitzgerald (University of Cambridge and Breathing Buildings) regarding a line plume against a solid boundary, it has been recommended that the coefficient be 0.08 and this value is therefore used.
Use of the tool in other applications
This simple tool can be used to help investigate some other scenarios. If a designer wishes to assess the entrainment as a result of uni-directional inflow through a horizontal damper in a space, then the flow can be approximated to leading order as a line plume emanating from all 4 sides of the damper. So, if the damper is 1.5m x 1.5m, the length of the window/damper should be given as 4x1.5m = 6m. The critical height is the height from the floor to the point at which mixing starts. It is easiest to state that the opening is a bottom hung window, and ensure that the height from the floor to the top of the opening in this model is then simply the height from the floor to the point where mixing can commence, which is usually at ceiling level.

## calcs (hidden)
SECONDARY SCHOOLS
alpha T | 0.08 | (standard value would be 0.102 but following discussion with Malcolm Cook in Dec 2016, and subsequent discussions with Paul Linden, Malcolm Cook, Henry Burridge, David Parker, Colm-cille Caulfield, Owen Connick and Shaun Fitzgerald in Mar 2018 it was agreed this should be reduced to 0.08)
C | 0.085668 | (not used)
Vl source | 0.053333 | cu m/s/m
Text | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | -1 | -2 | -3
g prime source | 0.1962 | 0.2289 | 0.2616 | 0.2943 | 0.327 | 0.3597 | 0.3924 | 0.4251 | 0.4578 | 0.4905 | 0.5232 | 0.5559 | 0.5886 | 0.6213 | 0.654 | 0.6867 | 0.7194 | 0.7521 | 0.7848
Bo | 0.012557 | 0.01465 | 0.016742 | 0.018835 | 0.020928 | 0.023021 | 0.025114 | 0.027206 | 0.029299 | 0.031392 | 0.033485 | 0.035578 | 0.03767 | 0.039763 | 0.041856 | 0.043949 | 0.046042 | 0.048134 | 0.050227
h virtual origin | 0.93177 | 0.88515 | 0.84665 | 0.81409 | 0.78602 | 0.76147 | 0.73972 | 0.72026 | 0.70271 | 0.68674 | 0.67214 | 0.65871 | 0.64629 | 0.63476 | 0.62401 | 0.61395 | 0.60451 | 0.59563 | 0.58725
g prime floor | 0.10585 | 0.12055 | 0.13485 | 0.14881 | 0.16247 | 0.17585 | 0.18898 | 0.20189 | 0.2146 | 0.22711 | 0.23944 | 0.25162 | 0.26363 | 0.27551 | 0.28724 | 0.29885 | 0.31033 | 0.3217 | 0.33296
delT | 3.237 | 3.6866 | 4.124 | 4.5509 | 4.9684 | 5.3776 | 5.7793 | 6.1741 | 6.5625 | 6.9452 | 7.3225 | 7.6947 | 8.0622 | 8.4253 | 8.7842 | 9.1391 | 9.4904 | 9.838 | 10.1823
T head | 17.763 | 17.3134 | 16.876 | 16.4491 | 16.0316 | 15.6224 | 15.2207 | 14.8259 | 14.4375 | 14.0548 | 13.6775 | 13.3053 | 12.9378 | 12.5747 | 12.2158 | 11.8609 | 11.5096 | 11.162 | 10.8177
Min allowed C | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Height from entry point of cold air to critical point | 0.8 | m
Top hung window | 0
Bottom hung hopper window | 0.5
Damper | 0.125
Distance added | 0
PRIMARY SCHOOLS
alpha T | 0.08 | (standard value would be 0.102 but following discussion with Malcolm Cook in Dec 2016, and subsequent discussions with Paul Linden, Malcolm Cook, Henry Burridge, David Parker, Colm-cille Caulfield, Owen Connick and Shaun Fitzgerald in Mar 2018 it was agreed this should be reduced to 0.08)
C | 0.085668 | (not used)
Vl source | 0.053333 | cu m/s/m
Text | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | -1 | -2 | -3
g prime source | 0.1962 | 0.2289 | 0.2616 | 0.2943 | 0.327 | 0.3597 | 0.3924 | 0.4251 | 0.4578 | 0.4905 | 0.5232 | 0.5559 | 0.5886 | 0.6213 | 0.654 | 0.6867 | 0.7194 | 0.7521 | 0.7848
Bo | 0.012557 | 0.01465 | 0.016742 | 0.018835 | 0.020928 | 0.023021 | 0.025114 | 0.027206 | 0.029299 | 0.031392 | 0.033485 | 0.035578 | 0.03767 | 0.039763 | 0.041856 | 0.043949 | 0.046042 | 0.048134 | 0.050227
h virtual origin | 0.93177 | 0.88515 | 0.84665 | 0.81409 | 0.78602 | 0.76147 | 0.73972 | 0.72026 | 0.70271 | 0.68674 | 0.67214 | 0.65871 | 0.64629 | 0.63476 | 0.62401 | 0.61395 | 0.60451 | 0.59563 | 0.58725
g prime floor | 0.09022 | 0.10233 | 0.11407 | 0.12549 | 0.13662 | 0.14751 | 0.15817 | 0.16862 | 0.17888 | 0.18898 | 0.19891 | 0.2087 | 0.21834 | 0.22786 | 0.23726 | 0.24654 | 0.25571 | 0.26479 | 0.27376
delT | 2.759 | 3.1294 | 3.4884 | 3.8376 | 4.1781 | 4.5109 | 4.8369 | 5.1565 | 5.4704 | 5.7791 | 6.0829 | 6.3821 | 6.6772 | 6.9683 | 7.2556 | 7.5395 | 7.82 | 8.0974 | 8.3719
T head | 18.241 | 17.8706 | 17.5116 | 17.1624 | 16.8219 | 16.4891 | 16.1631 | 15.8435 | 15.5296 | 15.2209 | 14.9171 | 14.6179 | 14.3228 | 14.0317 | 13.7444 | 13.4605 | 13.18 | 12.9026 | 12.6281
Min allowed C | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Height from entry point of cold air to critical point | 1.1 | m
Top hung window | 0
Bottom hung hopper window | 0.5
Damper | 0.125
Distance added | 0