## Sheet1
Date | Manufacturer | Door Type/Ref | Hardware | Glazed | Side | Time to failure (minutes) | Location of failure | Comment from Manufacturer
15/10/2018 | E&SW Knowles | DS20WAGCF5XXXXXX Finished Door Code - 1981x838x44 A.W. Oak 1500x150 7.2MM pyro FRSW322412125XXI 100x32 Liner 32x12 Stops 44x19 Archs Engineered Softwood Primed with Seals | Door handle Door closer | Yes | Opening into furnace | Test stopped after meeting 36 minutes. MHCLG policy was to end the test at this test house once 36-minutes was achieved and not to permit over-runs | N/A | "E&S W Knowles supply doorsets typically used in commercial buildings where glazing is required to comply with ADM. We are third-party certified under the IFCC doorset manufacturers’ scheme and designed the doorset based on assessed information from our IFC FOA report including a Strebord door core, Pyroguard glazing, Pyroplex seals and widely available hardware. The test overran as we would expect using these products, with the test being terminated after 36 minutes with no sign of failure on either specimen."
18/10/2018 | Gerda | Gerda Safer Homes Doorset. Style: Prosper (flush) | Door knocker Spyhole Letterbox Door closer | No | Opening into furnace | Test stopped after meeting 36 minutes. MHCLG policy was to end the test at this test house once 36-minutes was achieved and not to permit over-runs | N/A | "MHCLG requested that we provide five locations of installed doorsets and they chose one of these locations. Based on this we had to replicate the exact doorsets to be tested. These were flat entrance doorsets from within the Safer Homes Range and included letterbox, door viewer and door knocker in addition to other standard hardware. This range of doorsets is third party certified under the Q Mark scheme. Additional doorset styles within this range are tested in fire tests to EN1634-1 to both sides for both glazed and solid options and have achieved over-runs up to 50 minutes."
[5 empty] | Opening away from furnace | Test stopped after meeting 36 minutes. MHCLG policy was to end the test at this test house once 36-minutes was achieved and not to permit over-runs | N/A
25/10/2018 | West-Port | Thornthwaite Open In Fire Door, FD30s | Door handle Door closer | No | Opening into furnace | 46 | Centre of door leaf | "We are pleased to have been involved the MHCLG fire door investigation and satisfied that our doors conformed well above the testing regime standards. This is in line with our product range of 30 minute and 60 minute glazed secure by deign fire doors."
[5 empty] | Opening away from furnace | 41 | Top right corner
29/10/2018 | SFD Group | FD30s Single Door Set. Door Code SFD/FD30/1450X200 VP | Door handle Door closer | Yes | Opening into furnace | Test stopped after meeting 36 minutes. MHCLG policy was to end the test at this test house once 36-minutes was achieved and not to permit over-runs | N/A | "Very pleased with the work carried out by MHCLG on our fire door testing, it shows that working under BM trada 3rd party manufacturing scheme works well, and that clients can have confidence in our fire door."
[5 empty] | Opening away from furnace | Test stopped after meeting 36 minutes. MHCLG policy was to end the test at this test house once 36-minutes was achieved and not to permit over-runs | N/A
29/10/2018 | E&SW Knowles | DS20WAGCF5XXXXXX Finished Door Code - 1981x838x44 A.W. Oak 1500x150 7.2MM pyro FRSW322412125XXI 100x32 Liner 32x12 Stops 44x19 Archs Engineered Softwood Primed with Seals | Door handle Door closer | Yes | Opening away from furnace | Test stopped after meeting 36 minutes. MHCLG policy was to end the test at this test house once 36-minutes was achieved and not to permit over-runs | N/A | "E&S W Knowles supply doorsets typically used in commercial buildings where glazing is required to comply with ADM. We are third-party certified under the IFCC doorset manufacturers’ scheme and designed the doorset based on assessed information from our IFC FOA report including a Strebord door core, Pyroguard glazing, Pyroplex seals and widely available hardware. The test overran as we would expect using these products, with the test being terminated after 36 minutes with no sign of failure on either specimen."
30/10/2018 | Vicaima | Portaro SBD FD30s N1000 Oak Frame Code 610609 Door Code 610 611 | Keyhole Door handle Door closer | No | Opening into furnace | 54 | Top left corner | "As a specialist fire doorset manufacturer, with a long standing commitment to rigorous fire testing and third party accreditation, we welcomed this investigation and believe the MHCLG test vindicates Vicaima’s exemplary performance standards for entrance fire doorsets."
[5 empty] | Opening away from furnace | 48 | Bottom left corner
2018-12-11 | JELD-WEN | FD30 Paint Grade Door (CF192) | Door handle | No | Opening into furnace | 41 | Top left corner | N/A
[5 empty] | Opening away from furnace | 43 (no failure) | N/A
13/11/2018 | Door & Joinery Solutions | Internal paint grade fd30 fire door using Strebord 44 core | Door handle Door closer | No | Opening into furnace | 34 | Bottom left corner | "Door & Joinery Solutions are happy to have taken part in the MHCLG investigation. The over-performance is indicative of what we would expect to see from a well-constructed, timber doorset when using the Strebord door core from Falcon Panel Products and compatible assessed components and materials. Door & Joinery Solutions are certificated under the Certifire scheme. We are committed to third-party certification and understand the importance of manufacturing a high-quality, functional product designed to save lives in the unlikely event that it should be required to do so."
[5 empty] | Opening away from furnace | 49 | Top centre frame
14/11/2018 | Enfield Specialist Doors | ESD-FD30- Pas24 | Door handle Door closer | No | Opening into furnace | 35 | Top left corner | "Enfield Doors were pleased to have been approached and the factory visit by MHCLG personnel was a welcome one. We confidently supplied doorsets typically used in front entrance applications that require both fire, smoke and security performance (despite this having some large metal components that can prove a challenge when fire testing), because of the 3 point locking system. We are Third-Party Certified under IFCC doorset manufacturers’ scheme and based our manufactured specification using evidence of a previously tested doorset incorporating Strebord door core, STS seals and ERA hardware. It was positive to witness the test overrun and that the specimen opening away from the furnace performed beyond that of its opening inward counterpart, as it confirmed to us the long established rationale from assessment writers and current test standards."
[5 empty] | Opening away from furnace | 51 | Door handle
15/11/2018 | Deanta | Seville 44mm FD30 | Door handle Door closer | No | Opening into furnace | 42 | Top left corner | N/A
[5 empty] | Opening away from furnace | 56 | Door handle
16/11/2018 | Premdor | Premdor standard residential 30-minute fire doorset | Door handle | No | Opening into furnace | 50 | Top hinge | N/A
[5 empty] | Opening away from furnace | 49 | Head
2018-12-03 | Arnold Laver | Arnold Laver Internal FD30 Fire Door Set. | Door handle Door closer | No | Opening into furnace | 45 | Door handle | N/A
[5 empty] | Opening away from furnace | 46 | Door handle
2018-12-04 | Acorn | Averta doorset : Averta duo-touch FD30 door frame with Averta laminate FD30 glazed door | Door handle Door closer | Yes | Opening into furnace | 53 | Top left corner | "Really pleased to help MHCLG with their testing. Overjoyed to see the first of our FD30 doorset fail at 53 minutes and the other still intact when the test was stopped at 54 minutes."
[5 empty] | Opening away from furnace | 54 (no failure) | N/A
2018-12-10 | Ventro | N/A | Letterbox Door handle Door closer | No | Opening into furnace | 35 | Bottom centre frame | N/A
[5 empty] | Opening away from furnace | 41 | Bottom centre frame
2018-12-11 | G E Door Manufacturing | Latched, single action, single leaf FD30s | Keyhole Door handle | Yes | Opening into furnace | 35 | Top centre frame | N/A
[5 empty] | Opening away from furnace | 50 (no failure) | N/A
2018-12-12 | Doorpac | FD30 Strebord 44 | Keyhole Door closer | No | Opening into furnace | 45 | Top centre frame | N/A
[5 empty] | Opening away from furnace | 45 | Door handle
13/12/2018 | BBatch Group | N/A | Door handle Door closer | Yes | Opening into furnace | 40 | Glazing and top centre frame | N/A
[5 empty] | Opening away from furnace | 47 | Glazing
14/12/2018 | Ahmarra | Internal timber FD30 fire door | Keyhole Door handle | No | Opening into furnace | 47 | Door handle | "The results confirmed our expectation that Ahmarra’s fire doors will not only meet but will far exceed the expected fire resistance requirement. As well as undertaking our own primary fire testing, Ahmarra undergo a rigorous auditing process under BM TRADA – an impartial, third-party certification body. Offering our clients the reassurance of a fully certified and compliant product"
[5 empty] | Opening away from furnace | 56 | Door handle
15/12/2018 | Russel Timber Technology | QTE2 FD30S Door Set | Door handle | No | Opening into furnace | 48 (no failure) | N/A | N/A
[5 empty] | Opening away from furnace | 47 | Bottom left corner
16/12/2018 | Sentry Doors | FED20-44mm including letter plate and eye viewer | Letterbox Door handle Door closer | No | Opening into furnace | 43 | Bottom left corner - 14mm hardwood threshold | N/A
[5 empty] | Opening away from furnace | 30 | Bottom centre frame - 14mm hardwood threshold
15/02/2019 | Shellen Doors | Enduro Range Doorset | Door knocker Door handle Letterbox Door closer | No | Opening into furnace | 30 | Door handle | N/A
[5 empty] | Opening away from furnace | 30 | Door handle
16/02/2019 | Birmingham Joinery | 535803 | Door handle Door closer | No | Opening into furnace | 49 | Door handle | N/A
[5 empty] | Opening away from furnace | 56 | Bottom centre frame
23/02/2019 | Humphrey & Stretton plc | Vendor44 | Door closer | No | Opening into furnace | 46 | Top right frame | "At Humphrey & Stretton plc the quality and performance of our product is the most important part of what we do. Through years of product development we have confidence in our product and are delighted this has been proven by the government through this test."
[5 empty] | Opening away from furnace | 59 (no failure) | N/A
25/02/2019 | Shadbolt / Ruddy's Joinery | SHADMASTER 30 | Door closer Door handle Keyhole | No | Opening into furnace | 30 | Top right corner | N/A
[5 empty] | Opening away from furnace | 43 (no failure) | N/A
27/02/2019 | Doorset Technology | Stairwell Access, Unlatched, Single Acting | Door handle Door closer | Yes | Opening into furnace | 48 | Top left corner | “The achieved performance for both orientations fully endorses the previous and established test results typical for this application and rating, in that opening into the furnace is the most onerous condition. The 20% and 50% performance overruns are also consistent with the extensive bank of proven and reliable primary test evidence for this FD30S timber based doorset system”
[5 empty] | Opening away from furnace | 36 | Bottom left corner
16/03/2019 | Cotswold Manufacturing Ltd. | Xander - Q-Mark & BBA Doorset | Keyhole Door handle Door closer | Yes | Opening into furnace | 37 | Glazing | "As a fully accredited and certificated manufacturer of fire-rated timber products Cotswold Manufacturing Ltd welcomed and embraced the opportunity of supporting MHCLG by providing timber Doorset specimens in assisting with the Fire Door Investigation. MHCLG have our continued backing in promoting awareness and understanding of the importance of Doorsets, as a lifesaving devise, with the need of sourcing said products from a company such as CML that continue to invest in delivering product that exceed standards; which has been demonstrated by means of the test results exceeding our anticipated 20% overrun in achieving 37-40minutes resistance."
[5 empty] | Opening away from furnace | 40 | Glazing