## Sheet1
Test Commissioner	#	Test Date	Doorset	Style	Glazed	Manufacturer Date	Test standard	Test result (minutes)
Independent building owner	1	15/11/2017	Inside	SG08	No	2015	European	18
	2	13/12/2017	Inside	SG08	No	2014	British	25
	3	13/12/2017	Inside	SG08	No	2015	British	26
MHCLG	4	13/02/2018	Inside	SG34	Yes	2011	European	15
	5	24/02/2018	Inside	SG07	No	2011	British	27
	6	01/03/2018	Inside	SG15	Yes	2011	British	17.5
	7	06/04/2018	Inside	SG34	Yes	2012	British	28
	8	06/04/2018	Inside	SG11	Yes	2009	British	40
	9	11/04/2018	Inside	SG08	No	2014	British	21
	10	11/04/2018	Inside	SG08	No	2010	British	25
	11	22/04/2018	Inside	SG34	Yes	2012	British	23
	12	22/04/2018	Inside	SG11	Yes	2014	British	27
	13	25/04/2018	Inside	SG34	Yes	2011	British	25
	14	25/04/2018	Inside	SG34	Yes	2011	British	25
	15	26/04/2018	Inside	SG15	Yes	2012	British	14
	16	26/04/2018	Inside	SG34	Yes	2012	British	23
	17	03/05/2018	Inside	SG07	No	2014	British	31
	18	03/05/2018	Inside	SG07	No	2014	British	32
	19	11/05/2018	Inside	SG08	No	2012	British	20
	20	11/05/2018	Inside	SG08	No	2012	British	35

Test Commissioner	#	Manufacturer	Test Date	Glazed	Model/Company Ref.	Doorset	Test standard	Test result (minutes)	Mode of failure	Comment from Manufacturer
MHCLG	1	Masterdor Limited.	28/03/2018	Yes - half moon	GRP composite - half-moon glazed	Inside	British	16	Glazing	Following the indicative results received from the Ministry of Housing, Communities & Local Government’s (MHCLG) fire resistance tests of two Masterdor FD30 glazed GRP doors, Masterdor Limited (Masterdor) put in place a number of responsive measures, following consultation with MHCLG, which is ongoing. / • Independently, Masterdor suspended production of its GRP fire door range. / • An internal audit of accreditations found that full test evidence and global assessments were in place for all Masterdor products in the marketplace and for all third-party components that Masterdor relies upon in assembling its GRP fire door range. / • An industry-leading programme of research and development, underpinned by an intensive series of fire tests, was put in place – not only to test the performance of GRP doors further, but to also test the integrity and validity of the accreditations and global assessments issued to the company and upon which it had relied in manufacturing its product range. / Supporting this activity, a full communications programme was implemented with all of Masterdor’s affected customers. The communications issued so far have not only highlighted issues around door performance and issues around accreditations but have also provided updates on testing progress and shared protocols around fire assessments as laid out by MHCLG and its expert panel. / During this programme, close contact with Masterdor’s customers has been maintained through direct telephone calls, letters, emails and face-to-face meetings. A dedicated helpline was also implemented to offer advice and guidance to affected customers. / Masterdor continues to be proactive and responsive to its customers’ concerns and needs around this issue. The testing programme is continuing and the company remains in voluntary consultation with MHCLG. Masterdor is committed to playing a part in guiding the fire door industry through its role with Association of Composite Door Manufacturers (ACDM), particularly after the withdrawal of – by the fire testing houses that issued them – various global assessments and Field of Application reports upon which Masterdor had previously relied in good faith when manufacturing its range of GRP fire doors.
						Inside		23	Glazing
	2	Britdoors	12/07/2018	No	Richmond GRP / ORD0039591-0181	Inside	British	32	Passed	Both doorsets had letterplates fitted but there was no mechanical threshold, instead there was a 4mm airgap at the base of the door. / There was no failure of the letter plate, the threshold or any other componentry during the test. / The doors performed well and exceeded the prescribed time.
						Outside		33	Passed
	3	Permadoor	14/07/2018	No	Hughes	Inside	British	33	Passed	We take fire-door safety and testing seriously and rigorously conduct testing via appropriately accredited test facilities in accordance with Regulations. Whilst we were disappointed to see the test failure, which resulted from the failure of a replaceable glass component, we were pleased that the three clear passes demonstrated the strong performance of the product. / We are continuing work to identify the cause of the test result and which specific batches of glass this may relate to, as well as seeking greater clarity on the way in which the test was conducted. We are, however, pleased to note that in all other respects our products met the requirements of the test. Once we have completed our review, we will contact any customers who may be affected to agree any necessary actions.
						Outside		31	Passed
	4	Permadoor	23/07/2018	Yes - two panels	Larkin	Inside	British	35	Passed	Comments from Permadoor as above
						Outside		19	Glass
	5	Solar Windows	24/07/2018	Yes - two panels	Jacobean	Inside	British	21	Top left frame	Solar manufactures a range of fire doors in conformity with Global Assessments published by UKAS-approved test houses using components and suppliers specified by these Assessments. Solar’s manufacturing processes are strictly controlled in order to meet the standards specified in the authorized guidelines. Solar manufactures all its products to the following standards: / • BSI Quality Management System ISO 9001 : 2015 (Cert No. FM 24664) / • BSI 7412 (Cert No. KM 26965) in respect of windows made from PVC-U extruded hollow profiles / • BSI 7412 / PAS 24 (Cert No. KM 53036): Enhanced Security Windows Fabricator / • BS 7412/PAS 24 (Cert No. KM 646063): Enhanced Security PVC-U Doors Fabricator / • BS 8529 / PAS 24 (Cert No. KM 517937): Enhanced Security Composite Door Fabricator / • BSI Environmental Management System ISO 14001: 2015 – for the manufacture and management of installation of PVC-U windows and doors, and the purchase and manufacture of Composite Fire Doors / • Secured by Design Licence Holder / Solar has the following Industry Accreditations: / • Constructionline / • CHAS / • SMAS / • Safecontractor / • FENSA / • Secured by Design / • Exor / • LHC Appointed Contractor / • Association of Composite Door Manufacturers / Performance of fire doors is affected by a number of factors including product quality, design methodology, manufacturing processes and installation. For example, a combination of a frame, door slab and glazing sourced from one group of component suppliers will perform differently from a combination of a frame, slab and glazing sourced from a different group of suppliers. In other words, not all combinations perform the same. / Since the MHCLG tests in July 2018 Solar has carried out an extensive testing programme to BS 476 / EN1634 which is compulsory from September 2019 and in line with the Building Regulations in respect of all of its installed product range. These tests have established that components sourced within the supply chain may not in all cases satisfy the specified standards.
						Outside		45	Passed
	6	Birtley Group	28/07/2018	Yes - two panels	Bede / 540101/ 436236	Inside	British	39	Passed	The fire door issue is industry wide. Birtley Group has followed all of the directives with respect to containment action issued by the Fire Door Investigation Programme. Birtley Group has also carried out further testing of relevant products in an attempt to restore supply to our customers. The test regime is in accordance with the need to test on both sides of the door panel and we attach the relevant information arising from this testing. In summary, Birtley Group's recent testing has passed on both faces of the Bowater door above the 30-minute requirement and shows that the integrity of the Bowater door held at a minimum of 49 minutes and up to a maximum of 69 minutes. The Performance Certificates from the Rosenheim testing house confirming this have been provided to MHCLG and are available on request.
						Outside		24	Letterbox
	7	Sovereign	01/08/2018	No	Flat Flush	Inside	British	15	Bottom left frame	No comment provided
						Outside		29	Bottom right frame
	8	Birtley Group	03/08/2018	No	Includes letterbox and spyhole	Inside	British	9	Letterbox	Comments from Birtley Group are as above
						Outside		11	Letterbox
	9	Vista-Panels	04/08/2018	No	Edwardian Solid	Inside	British	25	Top left frame	No comment provided
						Outside		24	Bottom frame
	10	Britdoors	09/08/2018	Yes - half moon	Gloucester	Inside	British	23	Bottom frame	This failure was as a result of a part of the seal melting on the underside of the threshold which resulted in flaming after 23 minutes. We now fit as standard a higher performance fire seal to the threshold to prevent this type of failure. It should be noted that at the end of the 30 minute test period both doors were fundamentally still intact with no other failures recorded.
						Outside		8	Letterbox	This failure was a result of an error in the manufacturing process for this doorset whereby the letter plate was not correctly installed around the perimeter to one side the door. This resulted in a premature failure of the component.
	11	Sovereign	10/08/2019	No	Lune	Inside	British	30	Passed	No comment provided
						Outside		38	Passed
	12	Hurst Plastics	11/08/2019	Yes - half moon	ES01	Inside	British	37	Passed	No comment provided
						Outside		29	Left frame