5.0 Visual Inspection of the Installations

Mounded or Below Ground BFI - Visual Inspection Report
ID	The local identifier e.g. building or asset number
Type of installation	The type e.g. horizontal single or twin skin or NATO type vertical cylindrical single skin splinter protected etc. and its purpose e.g. aviation fuel for helicopter refuelling. Enter the manufacturer of the installation if known
Number of tanks	Number of tanks in the BFI
Capacity of each tank (litres)	As marked on the tank or from the records
Product	As marked on the tank or from the records
Date constructed (approx)	On the tank information plate or in the records
Date internally lined	The date of the last lining application
Last inspection date	As marked on the tank or from the records
Next inspection date	As marked on the tank or from the records
Last clean date	As marked on the tank or from the records
Next clean date	As marked on the tank or from the records
Last non destructive test type & date	Ultrasonic, MFL etc. report ref. & date completed
Number, make and model of FWS	From a visual inspection of equipment or records
Number, make and model of pumps	From a visual inspection of equipment or records
Number, make and model of FWM	From a visual inspection of equipment or records
Last dispense meter calibration	From the maintenance records
Last electrical test date	From the maintenance records
	Yes, No, Not Applicable or Not Known	Comment Reference No.
Condition of tanks: / Rust on exposed metal? / Access steps and handrails sound? / PV valves in good condition? / Evidence of leakage? / Paintwork acceptable? / Valve stems greased? / Cathodically protected? / Evidence of instability of mound? / Level gauging?
Comments: / Are the access steps and associated handrails to the top of the tank, handrails around the top and any tank top walkways sound? / Does the tank have PV valves or open vents? Do the PV valves look maintained and if open vents have protective mesh, are they clear of paint and other debris? / Are the tanks cathodically protected and are there any reported problems? / Does the earth mound look like it is becoming unstable, perhaps through the activity of rabbits or heavy rain? / Check for cracks or signs of leakage on weld joints, manways and reinforcing plates. / Record the type of gauging e.g. radar, servo etc. Check for damage, its general condition and whether there are reported problems.
Condition of pump and filter area: / Rust on piping? / Rust on equipment? / Paintwork acceptable? / Pressure gauges acceptable? / Differential pressure gauges acceptable? / Evidence of leakage? / Notices in order? / Schematic shown? / Neat and tidy? / Valve stems greased? / Filters last/next change date?
Comments: / Do the gauges and differential pressure gauges appear operational and calibrated? / Check for cracks or signs of leakage on weld joints and flanges.
Condition of dispense points: / Rust on piping? / Rust on equipment? / Paintwork acceptable? / Meter acceptable? / Pressure gauges acceptable? / Valve stems greased? / Hose condition acceptable? / Earth system acceptable?
Comments: / Do the gauges and differential pressure gauges appear operational and calibrated? / You should determine whether the hoses are pressure tested, you should record the test date and age of hose. / Is the earth system sound and secure?
Condition of road offload points: / Rust on piping? / Rust on equipment? / Paintwork acceptable? / Pressure gauges acceptable? / Valve stems greased? / Earth system acceptable?
Comments: / Do the gauges and differential pressure gauges appear operational and calibrated? / You should determine whether the hoses are pressure tested, you should record the test date and age of hose. / Is the earth system sound and secure?
Condition of control room: / Clean and tidy? / Level gauges working? / Temperature gauges working? / Fire panel working? / Alarms functioning? / Damaged equipment? / ATG regularly maintained? / ATG system backed up and stored in a separate safe location? / Silent hours leak detection alarms routed to permanently manned location? / ATG incorporates independent high/high alarms that stop pumps or isolates the installation?

Comments: / If there is an automatic tank gauging system, you should ask to see it working and confirm that the readings being displayed for level and temperature are reasonable. You should also ask the Operating Authority whether there are any known problems
Condition of generator house: / Generator in good condition? / Leaks in generator area? / Diesel bulk tank rusty? / Leaks from bulk tank? / Valve stems greased? / Bulk tank equipment acceptable? / Level gauges working? / Paintwork acceptable?
Comments: / Is the generator and oil tank system in a condition that gives cause for concern about its ability to function as intended?
Condition of secondary/tertiary containment: / Would a failure of the storage tank be detected or contained? / Would a failure of the ancillaries be detected or contained? / Risk assessment for tertiary containment completed? / Do the tertiary containment measures appear adequate?
Comments: / You should ask about the measures that are in place/deployable should there be a breach of the secondary containment or where there is no defined secondary containment. / The risk assessment can utilise COMAH, EA & CIRIA guidelines.
Condition of interceptor: / Operational and in sound condition? / Emptied regularly? / Clean and tidy? / Access available?
Comments: / Record whether access was available and if possible your observations regarding signs, general condition and any contamination observed.
Condition of electrical equipment: / Hazardous area classification plan? / Equipment appropriate for hazardous area in accordance with the ATEX equipment register? / Exposed SWA on gland terminations? / Unauthorised equipment modifications or additional holes? / Are tanks, FWS, pumps and supports earthed and earth straps across pipeline flanges? / Are earth tapes/conductors identified with equipment description? / Are main earth bars identified, including test point for mat/electrode? / Are junction boxes for Intrinsically Safe (IS) circuits clearly identified as such?
Comments: / Record whether there was a hazardous area classification plan available in accordance with the requirements of DSEAR. / Check the protection rating for equipment to determine whether it complies with the hazardous zone classification and equipment register
General comments: / Include comments on any other issues or observations here. / Are signs adequate? / What is the general housekeeping like? / State whether there is an up to date Certificate for Continued Operation displayed or FSAA available

Above Ground BFI - Visual Inspection Report
ID		The local identifier e.g. building or asset number
Type of installation		The type e.g. horizontal cylindrical or vertical, whether single skinned in a bund or integrally bunded and its purpose e.g. aviation fuel for aircraft refuelling. Enter the manufacturer of the installation if known.
Number of tanks		Number of tanks in the BFI
Last non destructive test type & date		Ultrasonic, MFL etc. report ref. & date completed
Number, make and model of FWS		From a visual inspection of equipment or records
Number, make and model of pumps		From a visual inspection of equipment or records
Number, make and model of FWM		From a visual inspection of equipment or records
Last dispense meter calibration		From the maintenance records
Last electrical test date		From the maintenance records
Condition of tanks: / For each storage tank in the installation, the following points should be addressed / Tank No. Local identifier Capacity (litres) From records Product From records / Constructed From records Date lined From records Last cleaned / Last inspection Next clean Next inspection / Last NDT type and date Ultrasonic, MFL etc. report ref. & date completed / Concrete ring or exposed foundation – / Is there broken concrete or cracks? Is there obvious settlement and is there vegetation against the bottom of the tank? / Tank – / Is there rust on exposed metal and is the paintwork acceptable? Are the access steps and associated handrails to the top of the tank, handrails around the top and any tank top walkways sound? Does the visible base appear sound and is the tank to visible base seal intact? Check for cracks or signs of leakage on weld joints, manways and reinforcing plates. Are cable connections to earthing lugs sound? Is there grooving, corrosion, pitting or coating failure on the visible internal surfaces of floating roof tanks? / Pipework – / Check for cracks or signs of leakage on weld joints and flanges. Is there rust on exposed metal and is the paintwork acceptable for the pipework, valves and other fittings? Are valve stems greased? / Secondary containment – You should address each of the questions below / Contains at least 110% of the largest tank or 25% of total storage, whichever is greatest? / Impermeable to water and/or oil? / Intact and without openings or valves for drainage? / Pipes that pass through sealed adequately? / Vent pipes, taps and valve arranged so that oil will be retained? / Signs of product staining? / Access acceptable? / Area outside the bund clear of signs of spillage? / Expansion joints in both bund floor and walls, intact? / Fire resistant structural integrity, joints and pipework penetrations? / Expanding fire resistant sealing to current standards? / Level gauge – / Record the type of gauging e.g. radar, servo etc. Check for damage, its general condition and whether there are reported problems.
PRVs – / Is there thermal pressure relief across main tank and main pipework isolating valves and does it look maintained? / Vents – / Does the tank have PV valves or open vents? Do the PV valves look maintained and if open vents have protective mesh, are they clear of paint and other debris? / Access – / Are the access steps and associated handrails to the top of the tank, handrails around the top and any tank top walkways sound? / General – / Is the tank cathodically protected and are there any reported problems? What is the general housekeeping like and are signs adequate? / Tank No. Local identifier Capacity (litres) From records Product From records / Constructed From records Date lined From records Last cleaned / Last inspection Next clean Next inspection / Last NDT type and date Ultrasonic, MFL etc. report ref. & date completed
		Yes, No, Not Applicable or Not Known	Comment Reference No.
Condition of pump and filter area: / Rust on piping? / Rust on equipment? / Paintwork acceptable? / Pressure gauges acceptable? / Differential pressure gauges acceptable? / Evidence of leakage? / Notices in order? / Schematic shown? / Neat and tidy? / Valve stems greased? / Filters last/next change date?
Comments: / Do the gauges and differential pressure gauges appear operational and calibrated? / Check for cracks or signs of leakage on weld joints and flanges.
Condition of dispense points: / Rust on piping? / Rust on equipment? / Paintwork acceptable? / Meter acceptable? / Pressure gauges acceptable? / Valve stems greased? / Hose condition acceptable? / Earth system acceptable?
Comments: / Do the gauges and differential pressure gauges appear operational and calibrated? / You should determine whether the hoses are pressure tested or visually inspected, you should record the test date and age of hose. / Is the earth system sound and secure?
Condition of road offload points: / Rust on piping? / Rust on equipment? / Paintwork acceptable? / Pressure gauges acceptable? / Valve stems greased? / Earth system acceptable?
Comments: / Do the gauges and differential pressure gauges appear operational and calibrated? / You should determine whether the hoses are pressure tested, you should record the test date and age of hose. / Is the earth system sound and secure?
Condition of control room: / Clean and tidy? / Level gauges working? / Temperature gauges working? / Fire panel working? / Alarms functioning? / Damaged equipment? / ATG regularly maintained? / ATG system backed up and stored in a separate safe location? / Silent hours leak detection alarms routed to permanently manned location? / ATG incorporates independent high/high alarms that stop pumps or isolates the installation?
Comments: / If there is an automatic tank gauging system, you should ask to see it working and confirm that the readings being displayed for level and temperature are reasonable. / You should also ask the Operating Authority whether there are any known problems.
Condition of generator house: / Generator in good condition? / Leaks in generator area? / Diesel bulk tank rusty? / Leaks from bulk tank? / Valve stems greased? / Bulk tank equipment acceptable? / Level gauges working? / Paintwork acceptable?
Comments: / Is the generator and oil tank system in a condition that gives cause for concern about its ability to function as intended?
Condition of secondary/tertiary containment: / Would a failure of the storage tank be detected or contained? / Would a failure of the ancillaries be detected or contained? / Risk assessment for tertiary containment completed? / Do the tertiary containment measures appear adequate?
Comments: / You should ask about the measures that are in place/deployable should there be a breach of the secondary containment or where there is no defined secondary containment. / The risk assessment can utilise COMAH, EA & CIRIA guidelines.
Condition of interceptor: / Operational and in sound condition? / Emptied regularly? / Clean and tidy?
Comments: / Record whether access was available and if possible your observations regarding signs, general condition and any contamination observed.
Condition of electrical equipment: / Hazardous area classification plan? / Equipment appropriate for hazardous area in accordance with the ATEX equipment register? / Exposed SWA on gland terminations? / Unauthorised equipment modifications or additional holes? / Are tanks, FWS, pumps and supports earthed and earth straps across pipeline flanges? / Are earth tapes/conductors identified with equipment description? / Are main earth bars identified, including test point for mat/electrode? / Are junction boxes for Intrinsically Safe (IS) circuits clearly identified as such?
Comments: / Record whether there was a hazardous area classification plan in accordance with the requirements of DSEAR available. / Check the protection rating for equipment to determine whether it complies with the hazardous zone classification and equipment register.
General comments: / Include comments on any other issues or observations here. / Are signs adequate? / What is the general housekeeping like? / State whether there is an up to date Certificate for Continued Operation displayed or FSAA available.

Semi Permanent Aviation Installations - Visual Inspection Report
ID		The local identifier e.g. building or asset number
Type of installation		Enter the manufacturer of the installation, the type e.g. horizontal cylindrical skid and its purpose e.g. aviation fuel for helicopter refuelling
Capacity of tank (litres)		As marked on the tank or from the records
Product		As marked on the tank or from the records
Date constructed (approx)		On the tank information plate or in the records
Single skin or integral containment		Single skin with separate bund or integral containment
Type of filters installed		E.g. coalescing, particulate etc.
Make and model of pump		From a visual inspection of equipment or records
Last dispense meter calibration		From the maintenance records
Last electrical test date		From the maintenance records
		Yes, No, Not Applicable or Not Known	Comment Reference No.
Condition of tanks: / Rust on exposed metal? / Adequate secondary containment? / Interstitial monitoring? / PV valve or open vent in good condition? / Evidence of leakage? / Paintwork acceptable? / Instruments acceptable? / Access to tank top acceptable?
Comments: / Is the secondary containment at least 110% of the volume of the primary containment, is there adequate means of monitoring the interstitial space and are there sufficient instruments to fulfil the required tasks? / Does the tank have a PV valve or open vent? Does the PV valve look maintained and if open vents have protective mesh, are they clear of paint and other debris?
Condition of pump/dispense area: / Rust on piping? / Rust on equipment? / Paintwork acceptable? / Meter acceptable? / Pressure gauges acceptable? / Differential pressure gauges acceptable? / Evidence of leakage? / Notice in order? / Planometric shown? / Neat & tidy? / Valve stems greased? / Filters last/next change date? / Adequate secondary containment? / Hose condition acceptable? / Earth system acceptable? / Alarms adequate?
Comments: / You should decide whether the gauges, any differential pressure gauges and meters appear operational and calibrated. / You should determine whether the hoses are pressure tested, record the date and age of hose. / Confirm that the earth system is sound and secure and that the flying lead is long enough. / You should confirm that the secondary containment is adequate for this part of the installation, that it can be emptied and that the relevant alarms are acceptable.
Condition of secondary/tertiary containment: / Would a failure of the storage tank be detected or contained? / Would a failure of the ancillaries be detected or contained? / Risk assessment for tertiary containment completed? / Do the tertiary containment measures appear adequate?
Comments: / You should ask about the measures that are in place/deployable should there be a breach of the secondary containment or where there is no defined secondary containment. / The risk assessment can utilise COMAH, EA & CIRIA guidelines.
Condition of interceptor for installation: / Served by an interceptor? / Operational? / Emptied regularly? / Clean & tidy?
Comments: / Record whether the area in which the installation is placed is served by an interceptor and if not, whether an appropriate environmental risk assessment has been completed. / If there is an interceptor, record whether access was available and if possible your observations regarding general condition and any contamination observed.
Condition of electrical equipment: / Hazardous area classification plan? / Equipment appropriate for hazardous area in accordance with the ATEX equipment register? / Exposed SWA on gland terminations? / Unauthorised equipment modifications or additional holes? / Are tanks, FWS, pumps and supports earthed and earth straps across pipeline flanges? / Are earth tapes/conductors identified with equipment description? / Are main earth bars identified, including test point for mat/electrode? / Are junction boxes for Intrinsically Safe (IS) circuits clearly identified as such?
Comments: / Record whether there was a hazardous area classification plan in accordance with the requirements of Dangerous Substances and Explosive Atmospheres Regulations (DSEAR) available and comment on any areas of disagreement with suggested changes. / Check the protection rating to determine whether it complies with the hazardous zone classification and equipment register.
General comments: / Include comments on any other issues or observations here. / Are signs adequate? / What is the general housekeeping like? / State whether there is an up to date Certificate for Continued Operation displayed or FSAA available.

Product Receipt Enclosure - Visual Inspection Report
	Yes, No, Not Applicable or Not Known	Comment Reference No.
Condition of PRE facility: / Rust on pipework? / Evidence of leakage? / Paintwork acceptable? / Pressure gauges acceptable? / Valves greased?
Comments: / Do the gauges and differential pressure gauges appear operational and calibrated?
Condition of microfilters: / Rust on pipe work? / Evidence of leakage? / Paintwork acceptable? / Pressure gauges acceptable? / Differential pressure gauges acceptable? / Flow indicators acceptable? / Dosing pots acceptable? / Valves greased?
Comments: / Do the gauges and differential pressure gauges appear operational and calibrated? / You should ask the Operating Authority whether there are any known problems with the filter.
Condition of back flush tank: / Rust on tank? / Rust on piping? / PV valve in good condition? / Evidence of leakage? / Paintwork acceptable? / Pressure gauges acceptable? / Level gauges acceptable? / Pump acceptable? / Valves greased?
Comments: / Does the PV valve on the back flush tank appear to be maintained? / If the level gauge is part of the fuel management system, you should you should ask to see it working and confirm that the readings being displayed are reasonable. / You should also ask the Operating Authority whether there are any known problems.
Condition of electrical equipment: / Hazardous area classification plan? / Equipment appropriate for hazardous area in accordance with the ATEX equipment register? / Exposed SWA on gland terminations? / Unauthorised equipment modifications or additional holes? / Are pumps and supports earthed and earth straps across pipeline flanges? / Are earth tapes/conductors identified with equipment description? / Are junction boxes for Intrinsically Safe (IS) circuits clearly identified as such?
Comments: / Record whether there was a hazardous area classification plan available in accordance with the requirements of DSEAR. / Check the protection rating to determine whether it complies with the hazardous zone classification and equipment register.
General comments: / Include comments on any other issues or observations here. / Comment on any common / linked safety, alarm and shut down systems between the site and the Oil and Pipeline Agency. / What is the general housekeeping like and are signs adequate? / Include comments on pigging facilities where they are included.

Pipeline - Visual Inspection Report
BFIs connected to pipeline	Use the local identifiers
Date constructed (approx)	From the records
Pipeline diameter	From the records or your measurement
Above or below ground	E.g. buried, partially buried or above ground
Last non destructive test type & date	E.g. pressure test, coating survey etc. report ref. & date completed
	Yes, No, Not Applicable or Not Known					Comment Reference No.
Condition of pipeline: / Is the route marked? / Is the pipeline cathodically protected? / Isolation flanges acceptable? / Adequate provision for thermal expansion? / Leak detection system acceptable? / Evidence/signs of leakage? / Pipeline supports acceptable? / Signs of ground settlement? / Is fuel reconciliation accurate enough to detect leaks?
Comments: / Are the routes of buried pipelines clearly identified with marker posts and have above ground pipelines been designed with adequate provision for thermal expansion? / Where cathodic protection is by impress current you should record any known problems and you should check both a sample of test points to ensure that they are intact and that isolation flanges look in good condition. / State location/position of the CP supply and control panel. / Where fitted, does the leak detection system have any known problems?
List of valve pits inspected:
Condition of valve pits: / Covers removable? / Rust on exposed metal? / Evidence of leakage? / Paintwork acceptable? / Valves acceptable? / Water accumulation? / Valve stems greased?	1	2	3	4	5	6	7	8	9	10
Comments: / When answering these questions you should consider whether the evidence indicates that the isolation, drain and vent valve pits are being maintained.
General comments: / Include comments on any other issues or observations here. Include comments on pigging facilities where they are included.

Hydrant Pipeline - Visual Inspection Report
BFIs connected to pipeline	Use the local identifiers
Date constructed (approx)	From the records
Pipeline diameter	From the records or your measurement
Last non destructive test type & date	E.g. pressure test, coating survey etc. report ref. & date completed
	Yes, No, Not Applicable or Not Known					Comment Reference No.
Condition of pipeline: / Is the route marked? / Is the pipeline cathodically protected? / Isolation flanges acceptable? / Leak detection system acceptable? / Evidence/signs of leakage? / Pipeline supports acceptable? / Signs of ground settlement? / Is fuel reconciliation accurate enough to detect leaks?
Comments: / Are the routes of buried pipelines in soft ground clearly identified with marker posts? / Where cathodic protection is by impress current you should record any known problems and you should check both a sample of test points to ensure that they are intact and that isolation flanges look in good condition. / State location/position of the CP supply and control panel. / Where fitted, does the leak detection system have any known problems?
Line valve pits inspected:
Condition of line valve pits: / Covers removable? / Rust on exposed metal? / Evidence of leakage? / Paintwork acceptable? / Valves acceptable? / Water accumulation? / Valve stems greased?
Comments: / This section refers to the main valve pits for the hydrant line to the dispersal area and de-fuel line if appropriate. / You should consider whether the evidence indicates that the isolation, drain and vent valve pits are being maintained.
Condition of Hydrant pits: / Covers removable? / Dust caps serviceable? / Signs of fuel leak? / Lanyard to the pilot valve intact? / Pilot valve operates without leaks? / Deadman’s handle intact? / Rust on seats? / Earth point sound?	1	2	3		4	5	6	7	8		9	10
Comments: / Some hydrant couplers will have a visible pilot valve to release pressure on the seat and no Deadman handle, which will be on the hydrant cart and some will not have a visible pilot valve, but will have a Deadman handle. / Where possible, opening and closing the pilot valves will indicate whether the main valve seats leak. / You should check the adjacent earth point to ensure that it is sound.
General comments: / Include comments on any other issues or observations here.

Mechanical Transport Fuelling Installations with Below Ground Storage Tanks - Visual Inspection Report
ID	Use the local identifiers
Type of installation	Single or twin skinned horizontal cylindrical etc. and material. Most tank installations will be below ground, but if above ground, an Above Ground Ancillary Storage Tank Installation sheet must be completed in addition, which will include comment on the underground pipework.
Number of tanks	Number of tanks in the installation
Type of leak detection	From the records
Capacity of each tank (litres)	As marked on the tank or from the records
Type of wet stock management system	Automatic (record manufacturer) and/or dips / This may include an Automatic Fuelling Dispensing System (AFDS) and/or an automatic tank gauging (ATG) system
Number, make and model of dispensers	From a visual inspection of equipment or records
Product	As marked on the tank or from the records
Date constructed (approx)	As marked on the tank or from the records
Electrical supply arrangements	Record whether TT, TN-S or TNC-S / Where an existing electrical installation is supplied from a TNC-S system in which the neutral and protective functions are combined in part of the system to provide PME, stray currents passing through metalwork located in potentially hazardous areas may pose an increased risk of fire or explosion.
Make, type and capacity of OWI	From the records or data plate
Last non-destructive test type & date	E.g. precision tank tightness test (integrity test) etc. report ref. & date completed
Last dispense pump calibration	From the maintenance records
Last electrical test date	From the maintenance records
	Yes, No, Not Applicable or Not Known	Comment Reference No.
Condition of tanks: / Rust on exposed metal? Paintwork acceptable? / Evidence of leakage? / Leak detection system working? / Manway free of product? / Manway free of water? / Vents clear from obstruction – 3m radius? / Tanks and vents correctly labelled? / Vapour recovery system fitted? / Vapour recovery system operating instructions available?
Comments: / If there is leak detection installed, are there any known problems with the system?
Condition of fuel dispenser pumps: / Rust on exposed metal? / Evidence of leakage? / Staining of floor? / Paintwork acceptable? / Hose condition acceptable? / Pistol condition acceptable? / Dispense pump condition acceptable? / Stage 2 vapour recovery fitted?
Comments: / The hose should be sound, free of serious damage and fitted with safety break couplings. / For all self service installations the latching pins should be removed from the pistol and the pistol should be free from leaks.
Forecourt surfaces: / Impermeable material used? / Cracks in surface? / Joints in sound condition? / Perimeter drainage adequate and clear of debris? / Does the OWI have a visual or audible alarm? / Is any diesel exhaust fluid stored correctly?
Comments: / Record the material used for the forecourt and its general condition / If the OWI is a forecourt model, it will be fitted with an auto-closure device and alarm / As diesel exhaust fluid (AdBlue) is an aqueous urea solution, it must be stored properly
Condition of electrical equipment: / Hazardous area classification plan? / Equipment appropriate for hazardous area in accordance with the ATEX equipment register? / Exposed SWA on gland terminations? / Unauthorised equipment modifications or additional holes? / Are main earth bars identified, including test point for mat/electrode?
Comments: / Record whether there was a hazardous area classification plan in accordance with the requirements of DSEAR available. / Check the protection rating for equipment to determine whether it complies with the hazardous zone classification and equipment register.
General comments: / Include comments on any other issues or observations here. / What is the general housekeeping like and are signs adequate? / State whether there is an up to date Certificate for Continued Operation displayed or FSAA available. / State whether there are any issues with the interceptor. / Are fire extinguishers available and regularly inspected?

Underground Tank and Pipework Assessment
ID	Use the local identifiers
	Yes, No, Not Applicable or Not Known	Comment Reference No.
Level 1 assessment undertaken?		Appropriate for steel tanks only
Non-destructive testing undertaken?		Appropriate for single skinned tanks but may also include single skinned pipework associated with double skinned tanks
Further testing required?		Based on age, last test or the inspector’s opinion
Comments: / You should comment on the impact of the scoring from the level 1 assessment, the requirement for further non-destructive testing and you should recommend the type of test that is appropriate.

Mechanical Transport Fuelling Installations with Above Ground Storage Tanks - Visual Inspection Report
ID	Use the local identifiers
Type of installation	Single or twin skinned horizontal cylindrical etc. and material. If the tank is used for storage of class I product, comment on construction standards for the tank UL2085 etc.
Number of tanks	Number of tanks in the installation
Type of leak detection	From the records
Capacity of each tank (litres)	As marked on the tank or from the records
Type of wet stock management system	Automatic (record manufacturer) and/or dips / This may include an Automatic Fuelling Dispensing System (AFDS) and/or an automatic tank gauging (ATG) system
Number, make and model of dispensers	From a visual inspection of equipment or records
Product	As marked on the tank or from the records
Electrical supply arrangements	Record whether TT, TN-S or TNC-S / Where an existing electrical installation is supplied from a TNC-S system in which the neutral and protective functions are combined in part of the system to provide PME, stray currents passing through metalwork located in potentially hazardous areas may pose an increased risk of fire or explosion.
Make, type and capacity of OWI	From the records or data plate
Date constructed (approx.)	As marked on the tank or from the records
Last non-destructive test type & date	E.g. precision tank tightness test (integrity test) etc. report ref. & date completed
Last dispense pump calibration	From the maintenance records
Last electrical test date	From the maintenance records
	Yes, No, Not Applicable or Not Known	Comment Reference No.
Location: / Is the tank situated more than 10 metres from a watercourse? / Is the tank situated more than 50 metres from a well or borehole? / Is the tank protected from impact damage?
Comments: / 1. Refer to the appropriate regulations for the UK and/or host nation relevant to where fuel installation is located.2.Does the tank have adequate mechanical protection, especially if it does not sit in a conventional bund?
Condition of tank: / Rust on exposed metal? Paintwork acceptable? / Is the underside of the tank accessible for inspection? / Access steps and handrails sound? / Evidence of leakage? / Bund alarm fitted to integrally bunded tanks? / Automatic over fill protection device fitted and working? / Vents clear from obstruction – 3m radius? / Instruments acceptable? / Sight gauge properly supported and protected from damage? / Sight gauge fitted with self-closing valve? / Tank drain valve locked or blanked? / Outlet valve from tank located within secondary containment? / Syphon outlet from tank, anti-syphon valve fitted? / Correct signage displayed for the tank and its contents?
Comments: / If there is leak detection installed, are there any known problems with the system? / Comment if the tank is so badly corroded that in your opinion it is likely to leak. / Signs should include tank ID, product and capacity as a minimum.
Condition of fuel dispenser pumps: / Rust on exposed metal? / Evidence of leakage? / Paintwork acceptable? / Hose condition acceptable? / Pistol condition acceptable? / Dispense pump condition acceptable? / Stage 2 vapour recovery fitted?
Comments: / The hose should be sound, free of damage and fitted with safety break couplings. / For all self service installations the latching pins should be removed from the pistol and the pistol should be free from leaks.
Forecourt surfaces: / Impermeable material used? / Cracks in surfaces? / Joints in sound condition? / Road tanker delivery stand correct size? / Perimeter drainage adequate and clear of debris? / Does the OWI have a visual or audible alarm? / Is any diesel exhaust fluid stored correctly?
Comments: / Record the material used for the forecourt and its general condition / If the OWI is a forecourt model, it will be fitted with an auto-closure device and alarm / As diesel exhaust fluid (AdBlue) is an aqueous urea solution, it must be stored properly / The road tanker delivery stand should be a minimum of 15m long x 5m wide.
Secondary containment: / At least 110% of the largest tank or 25% of total storage, whichever is greatest? / Impermeable to water or oil? / Intact and without openings or valves for drainage? / Pipes that pass through sealed adequately? / Are vent pipes, taps and valve arranged so that oil will be contained? / Signs of product staining? / Access acceptable? / Adequate leak detection for underground pipework? / Leak detection maintained?
Comments: / Is there evidence that the integrity of the bund may be suspect and is the overall condition satisfactory?
Condition of ancillaries: / Ancillaries within secondary containment? / Fill point acceptable? / Tank vent visible from fill point? / Protected from impact and damage? / Protected from corrosion? / Paintwork acceptable? / Evidence of leakage? / Adequate leak detection for underground pipework? / Leak detection maintained?
Comments: / Underground pipelines should not have mechanical joints unless it is possible for them to be inspected.
Condition of exposed pipework: / Rust on exposed metal? / Evidence of leakage? / Paintwork acceptable? / Lagging intact, where fitted? / Valve stems greased? / Mechanical joints satisfactory?
Comments: / Inspect the exposed mechanical joints for evidence of failure.
Condition of electrical equipment: / Hazardous area classification plan? / Equipment appropriate for hazardous area in accordance with the ATEX equipment register? / Exposed SWA on gland terminations? / Unauthorised equipment modifications or additional holes? / Are main earth bars identified, including test point for mat/electrode?
Comments: / Record whether there was a hazardous area classification plan in accordance with the requirements of DSEAR available. / Check the protection rating for equipment to determine whether it complies with the hazardous zone classification and equipment register.
General comments: / Include comments on any other issues or observations here. / What is the general housekeeping like and are signs adequate? / State whether there is an up to date Certificate for Continued Operation displayed or FSAA available. / State whether there are any issues with the interceptor. / Are fire extinguishers available and regularly inspected?

Flammable Dangerous Goods Store - Visual Inspection Report
ID	Use the local identifiers
Type of structure	Record the structure type
Date constructed (approx)	From the records
	Yes, No, Not Applicable or Not Known	Comment Reference No.
Storage: / Substances segregated by UN Class? / Substances separated by minimum distances? / Separate area for repacking of damaged containers? / Separate room for acid storage?
Comments: / You should comment on what is being stored by UN Class and any departures from the requirements of Design and Maintenance Guide 03 – Storage of Dangerous Substances, Section 3 Product Segregation.
Store construction: / All walls fire rated? / Explosion relief roof design? / Storage areas bunded? / Prevention of aqueous substances from reaching the drainage system?
Comments: / You should comment on whether the structure is purpose built and complies to the requirements of Design and Maintenance Guide 03 – Storage of Dangerous Substances, Section 4 Storage Buildings/Compounds.
Building services: / Equipment appropriate for hazardous area in accordance with the ATEX equipment register? / Fire fighting equipment? / Lightning protection? / Emergency telephone? / Adequate ventilation? / Drench shower and eyewash for acid store? / Are appropriate signs displayed?
Comments: / Are the appropriate UN Class product signs displayed on the door or access gate? / Are there signs in accordance with the requirements of DSEAR? / Steel stores and other structures may not need lightning protection in accordance with guidance contained in BS EN 62305.
General comments: / Include comments on any other issues or observations here. / What is the general housekeeping like? / Record whether there was a hazardous area classification plan in accordance with the requirements of Dangerous Substances and Explosive Atmospheres Regulations (DSEAR) available.

Above Ground Ancillary Storage Tank Installations – Visual Inspection Report
ID	Use the local identifiers
Type of installation	E.g. horizontal or vertical, cylindrical or rectangular, single skinned with separate secondary containment or integrally bunded and its purpose e.g. standby generator or heating. Record the material of construction and enter the manufacturer of the installation if known.
Number of tanks	Number of tanks in the installation
Type of fuel measurement system	As observed on the tank
Type of leak detection	From the records
Capacity of each tank (litres)	As marked on the tank and from the records
Product and classification	As marked on the tank and from the records
Date constructed (approx)	As marked on the tank and from the records
Last non destructive test type & date	E.g. precision tank tightness test (integrity test) etc. report ref. & date completed
Last inspection date	From the records
	Yes, No, Not Applicable or Not Known	Comment Reference No.
Location: / Is the tank situated more than 10 metres from a watercourse? / Is the tank situated more than 50 metres from a well or borehole? / Is the tank protected from impact damage?
Comments: / 1. Refer to the appropriate regulations for the UK and/or host nation relevant to where fuel installation is located 2. Does the tank have adequate mechanical protection, especially if it does not sit in a conventional bund?
Condition of tanks: / Rust on exposed metal? / Evidence of leakage? / Is the underside of the tank accessible for inspection? / Paintwork acceptable? / Instruments acceptable? / Correct signage displayed for the tank and its contents? / Bund alarm fitted to integrally bunded tanks? / Outlet valve from tank located within secondary containment? / Syphon outlet from tank, anti-syphon valve fitted? / Tank drain valve locked or blanked? / Automatic over fill protection device fitted and working? / Sight gauge properly supported and protected from damage? / Sight gauge fitted with self-closing valve?
Comments: / Comment if the tank is so badly corroded that in your opinion it is likely to leak. / Signs should include tank ID, product and capacity as a minimum.
Secondary containment: / At least 110% of the largest tank or 25% of total storage, whichever is greatest? / Impermeable to water or oil? / Intact and without openings or valves for drainage? / Pipes that pass through sealed adequately? / Are vent pipes, taps and valve arranged so that oil will be contained? / Signs of product staining? / Access acceptable? / Adequate leak detection for underground pipework? / Leak detection maintained?
Comments: / Is there evidence that the integrity of the bund may be suspect and is the overall condition satisfactory?
Condition of ancillaries: / Ancillaries within secondary containment? / Tank vent visible from fill point? / Protected from impact and damage? / Protected from corrosion? / Paintwork acceptable? / Valves locked when not in use? / Evidence of leakage? / Fill point acceptable? / Flexible connections/draw-off pipes fitted? / Auto closure valve fitted to flexible? / Flexible stowed correctly when not in use? / Flexible pipework <10 years old? / Pump set fitted? / Non-return valve fitted to pump set suction line? / Pump set protected from misuse or accidental damage?
Comments: / Underground pipelines should not have mechanical joints unless it is possible for them to be inspected.
Condition of exposed pipework: / Rust on exposed metal? / Evidence of leakage? / Paintwork acceptable? / Lagging intact, where fitted? / Valve stems greased? / Mechanical joints satisfactory?
Comments: / Inspect the exposed mechanical joints for evidence of failure.
General comments: / Include comments on any other issues or observations here. / What is the general housekeeping like?

Underground Ancillary Storage Tank Installations – Visual Inspection Report
ID	Use the local identifiers
Type of installation	E.g. horizontal cylindrical and its purpose e.g. standby generator or heating. Record the material of construction and enter the manufacturer of the installation if known.
Number of tanks	Number of tanks in the installation
Type of fuel measurement system	As observed on the tank
Type of leak detection	From the records
Capacity of each tank (litres)	As marked on the tank and from the records
Product and classification	As marked on the tank and from the records
Date constructed (approx)	As marked on the tank and from the records
Last non destructive test type & date	E.g. precision tank tightness test (integrity test) etc. report ref. & date completed
Last inspection date	From the records
Next inspection date	From the records, from the age or from the condition
	Yes, No, Not Applicable or Not Known	Comment Reference No.
Condition of tanks: / Rust on exposed metal? / Evidence of leakage? / Paintwork acceptable? / Contents gauges, overfilling alarm/device acceptable? / Tank interstitial space leak detection acceptable? / Correct signage displayed for the tank and its contents?
Comments: / Comment of the visible aspects of the tank. / Signs should include tank ID, product and capacity as a minimum.
Condition of ancillaries: / Instruments acceptable? / Tank vent visible from fill point? / Automatic over fill protection device fitted and working? / Protected from corrosion? / Paintwork acceptable? / Valves locked when not in use? / Evidence of leakage? / Adequate leak detection for underground pipework? / Leak detection maintained? / Pump set fitted? / Pump set protected from misuse or accidental damage?
Comments: / Underground pipelines should not have mechanical joints unless it is possible for them to be inspected.
Condition of exposed piping: / Rust on exposed metal? / Evidence of leakage? / Paintwork acceptable? / Lagging intact, where fitted? / Valve stems greased? / Mechanical joints satisfactory?
Comments: / Inspect the exposed mechanical joints for evidence of failure.
General comments: / Include comments on any other issues or observations here.

Underground Tank and Pipework Assessment
ID	Use the local identifiers
	Yes, No, Not Applicable or Not Known	Comment Reference No.
Level 1 assessment undertaken?		Appropriate for steel tanks only
Non-destructive testing undertaken?		Appropriate for single skinned tanks but may also include single skinned pipework associated with double skinned tanks
Further testing required?		Based on age, last test or the inspector’s opinion
Comments: / You should comment on the impact of the scoring from the level 1 assessment, the requirement for further non destructive testing and you should recommend the type of test that is appropriate.

  1. Inspection of Maintenance RECORDS AND SUPPORTING INFORMATION

6.1 Spillage Response Plans

Record here whether spillage response plans are available, note the date that they were last amended and issued, the name and role of the signatory and any other pertinent comments.

6.2 Installation Records

Record here your comments on the installation records, noting in particular whether there is original design data, design drawings, P&IDs and information on repairs, modifications and other changes

6.3 Dangerous Substances Explosive Atmosphere Regulations (DSEAR) Records

Confirm here whether the following documentation is available:
1. MoD Form 5014 Stage 1
2. MoD Form 5014 Stage 2
3. Flammable Materials List & Characteristics
4. Source of Release Risk Assessments
5. Retrospective Ignition Risk Assessments for Non-Electrical Equipment for use in Potentially Explosive Atmospheres
6. Facility Risk Assessments
7. A site drawing indicating the location of all classified hazardous areas identified
8. Drawings of each asset or installation incorporating a classified hazardous area on a separate drawing shown in plan view and in section or elevation as appropriate. The plan view shall show the classified hazardous areas in context to the site features within 2 metres of the hazardous zone. This should include buildings, culverts or other man-made structures and clearly indicate the required temperature class and gas group for any equipment to be used in that area.

6.4 Inspection, Maintenance and Testing Regime

Record here whether there is an Inspection, Maintenance and TestingA Regimein accordance with the requirements of Inspection, Maintenance and Testing of Equipment Installed at Petroleum Installations on MOD Property’ Technical Standard Petroleum – 01. The document is to clearly identify the inspection and testing regime to ensure that the entire electrical installation is subject to the following:
1. 12 month Visual Inspection in accordance with BS EN 60079 part 17 - 50% of installation
2. 12 month Close Inspection in accordance with BS EN 60079 part 17 - 50% of installation
3. 36 months Detail in accordance with BS EN 60079 part 17 - 100% of installation (this may be carried out 33.3% every 12 months)

Record whether the above aligns with the planned maintenance schedule and the equipment registers for the installations.

Confirm whether records of inspection, maintenance and testing are accessible to those undertaking these tasks, whether they are kept for the life of the equipment/installation and whether they are compared against current records to identify any deterioration that is taking place.

Confirm that a verification dossier in accordance with the requirements of BS EN 60079-14 is available for the electrical installations and that the dossier has been updated to reflect any changes since the original installation date.

6.5 List of Maintenance Work

Following the visual inspection, a review of the maintenance regime was carried out. The maintenance work is managed using (record here the name of the system being used) computer based system, the scope of which is based upon the extant Technical Standard for ‘Inspection, Maintenance and Testing of Equipment Installed at Petroleum Installations on MOD Property' Technical Standard Petroleum – 01 and Technical Standard Petroleum - 04.

Evidence was sought for the following:

List here those installations checked and the tasks e.g. MTFI mechanical maintenance and calibration
6.6 Maintenance Register

A maintenance register should be kept listing all maintenance operations, their frequencies of requirement, special notes on repairs carried out and any observations of problems noticed.

The extant Technical Standard for ‘Inspection, Maintenance and Testing of Equipment Installed at Petroleum Installations on MOD Property' Technical Standard Petroleum – 01 and Technical Standard Petroleum – 04 define the frequency at which the various items of equipment should be maintained.

Mechanical Maintenance Register - Document Inspection Report
ID	Record here the local identifier e.g. Building Number
Tasks checked:
	Yes, No, Not Applicable or Not Known	Comment Reference No.
Are all the tasks above being completed? / Are the tasks completed at the correct frequency? / Are all the tasks dated correctly? / Are all the tasks signed off?
Is the equipment shown as satisfactory/not satisfactory? / If “not" does the register record the reasons? / Is incidental or repair work recorded in the register?
Are the separator element changes recorded? / If "Yes" does date match that on the separator body?
General comments: / You should record the maintenance tasks that you have checked and the dates that they were last completed. / E.g. Jacket No. 1 for BFI No. 2 – Last 3 monthly tasks completed 01/04/08. / You should also comment on the maintenance standard being followed, relevant tasks not being completed and disparities between the records and observations during the site visit.

Electrical Maintenance Register - Document Inspection Report
ID	Record here the local identifier e.g. Building Number
Tasks checked:
	Yes, No, Not Applicable or Not Known	Comment Reference No.
DSEAR compliance survey completed?
Is there a Hazardous Area classification drawing available in accordance with the requirements of DSEAR?
Is there an equipment register available, does it align with installed equipment, including tag identification?
Are all the above tasks being completed? / Are the tasks completed at the correct frequency? / Are all the tasks dated correctly? / Are all the tasks signed off?
Is the equipment shown as satisfactory/not satisfactory? / If “not" does the register record the reasons? / Is incidental or repair work recorded in the register?
Are appropriate earth checks completed?
Are electrical test reports completed in accordance with Section 17 of PG 2017/02 and for installations other than MTFI acknowledged by the MMO on test sheet Form 1a?
Are alarms and shutdown functions tested in accordance with Technical Standard Petroleum - 02?
Are motors subject to condition monitoring (see jobs 23.2 & 23.3 of Technical Standard Petroleum - 02?
Are motor protective devices tested every 5 years?
General comments: / You should record the maintenance tasks that you have checked and the dates that they were last completed. E.g. Jacket No. 1 for BFI No. 2 – Last hazardous area electrical test completed 01/04/08. / Include comments on any other issues or observations here.

APPENDIX A MMO ANCILLARY TANK INSTALLATION DECLARATION

All ancillary tank installations comply with current legislation, which include The Control of Pollution (Oil Storage) (England) Regulations, Control of Pollution (Oil Storage) Regulations Northern Ireland or The Water Environment (Oil Storage) (Scotland) Regulations along with associated guidance for above ground storage tanks (ASTs); and the Groundwater Regulations 1998 along with associated guidance for underground storage tanks (USTs).

With the exception of:

Tank Location	Tank ID	Construction	Size (litre)	Product	Deficiencies

An action plan is in place to carry out the remedial works listed above which should be completed by {date}

An appropriate maintenance regime is in place and implemented for all ancillary tank installations.

The following ancillary tank installations do not comply with current legislation, no funding has been released from the client following the previous inspection and these installations are to be included within the main inspection regime completed in accordance with the extant Technical Standard for the Inspection of Petroleum Installations and Flammable Dangerous Goods Stores.

Tank Location	Tank ID	Construction	Size (litre)	Product	Deficiencies

Signed:	Date:

{Name}

{Position}

{Company Name}

APPENDIX B Ancillary installations ASSET LIST

Ancillary Installations / Above ground storage tanks (ASTs) – Underground storage tanks (USTs)
	Asset / building number		Installation / / Product	Tank size (Capacity) Litres		Date installed		Type	Material	Compliance Assessments / inspections/ integrity tests completed / No, Not Known or date completed				Remedial works required		Comment
					ASTs	USTs	Underground pipework	PPM task
	Local identifier	Serving a boiler or generator and product					Horizontal, cylindrical above ground etc.		Steel, fibreglass, HDPE etc.

General comments: / Has the MMO completed a tank inspection declaration? / Is the tank declaration acceptable? / The asset list on the pre-planned maintenance data base, MIS IFS, requires updating: ……… / The above asset list is complementary to the Spill Plan for……… USRP – which has a comprehensive list of the petroleum tank installations for the sites, but does not include the Flammable Dangerous Goods Stores (FDGS). / AST = Above ground storage tank. UST = Under-ground storage tank. HDPE = High Density PolyEthylene (Plastic). PPM = Pre-Planned Maintenance. / Tanks within buildings and underground storage tanks (USTs) do not have to comply with SI 2001 No 2954 and the respective Pollution Prevention Guides (PPGs); however integrity and control must still be maintained in accordance with the Ground Water Regulations. USTs should be assessed in accordance with the extant Practitioner Guide for the Inspection of Petroleum Installations and Flammable Dangerous Goods Stores. / The following also requires to be referenced: - / OFTEC Standards: OFS T 100 - plastic tanks; OFS T 200 - steel tanks; T 19 tank base construction / CIRIA publications: CIRIA 163 bunds; CIRIA 535 above ground tanks / DEFRA: Guidance document: Ground Water Protection Code (Water Resources Act and Groundwater Regulations) / (Note reference required as pipework may be sited under-ground) / There are a number of British Standards, for sectional steel tanks, USTs, ASTs, steel cylindrical tanks, GRP tanks and rigid plastic tanks etc. Most of which are referenced in the above, and would be applicable to the manufacturer and their manufacturing processes. / B.S. 5410 part 1. – Domestic < 45kw; B.S. 5410 part 2. – Industrial / commercial > 45kw. B.S. 799 – Steel tanks