Safety Alert Parts A, B, & C				Health and Safety
Subject: Schneider/Merlin Gerin – Genie SF6 failure / Number: SA 2021/10
DIO Sponsor: Bryan Dunn			Date of issue: 21st December 2021
Contact if different from above Sponsor: / John Hancock / Technical Services, Engineering & Construction / Defence Infrastructure Organisation. / DMS Whittington, Lichfield. Staffordshire. WS14 9PY / Email: john.hancock109@mod.gov.uk / Tel: +44 (0) 7977 345915
This Safety Alert is to be read by the following so appropriate action can be taken: / DIO’s Maintenance Management Organisations and their Supply Chains / DIO Regional Delivery Manager (or equivalent for non-NGEC contracts) / Head of Establishments / Others / Others interested in the content of this Safety Alert might include: / Assurance Managers, Estate Facility Managers, Assurance Managers in Regional (Service) Delivery Health & Safety Advisors, Top Level Budget Holders, Prime Contractors, Project Managers, Infrastructure Managers and Property Managers with responsibility for MOD projects and Property Management Works Services (including the legacy work of EWCs/WSMs), Authorised Persons (Electrical), Authorising Engineer (Electrical) etc.
When it takes effect: Immediately		When it is due to expire: When updated or rescinded.
	This Safety Alert does not necessarily cover all aspects of the subject matter and readers should make themselves aware of other potential issues. Readers should also not rely on DIO Publications as their only means of becoming aware of safety issues, but they should consult widely across other media to maintain awareness.

Aims
1. The aims of this Safety Alert are to bring to the attention of appropriate persons or organisations:
  1. The need to ensure that prior to operation the panel within a Genie SF6 switchboard has satisfactory positive gas pressure.
  2. Ensure during routine maintenance a check that the low gas pressure inhibit links are installed.
Introduction
1. Compliance with the contents of this Safety Alert will enable compliance with the Health & Safety at Work etc. Act 1974 and Electricity at Work Regulations 1989.
2. Any work required as a result of this Safety Alert must be carried out in accordance with the Management of Health & Safety in Ministry of Defence – JSP375 Volume 3.
Background
1. The Energy Networks Association (ENA) Dangerous Incident Notification (DIN) 2021/0019/00 advises of an incident on a Merlin Gerin Genie SF6 switchboard.
2. Whilst working on a Merlin Gerin Genie SF6 11Kv switchboard, an adjacent panel failed disruptively, which resulted in one of the operatives suffering minor injuries. (See photographs at Annex A.)
3. The neighbouring module was known to contain low / no SF6 gas and was left in the closed ‘in service’ position with a ‘dead operation only’ operational restriction assigned to it.
4. Based on the wiring configuration of the panel, the tripping of the circuit breaker could only be achieved by one of the following means:
  1. Operation of the mechanical push button
  2. Operation of the protection relay fitted to the circuit breaker, which should be inhibited by the wiring link, to prevent the operation of the breaker when low gas is detected
5. The investigation has failed to identify the root cause of the inadvertent opening of the circuit breaker but could have been due to:
  1. Personnel making accidental contact with the mechanical push button of the circuit breaker (which was found to be unlocked)
  2. A downstream cable fault resulting in the operation of the protection relay (the relay was damaged by the incident and the event log is not available.)
6. This Safety Alert concerns all Merlin Gerin Genie SF6 switchboards. These are not to be confused with Merlin Gerin Genie Evo range which in appearance look similar but use vacuum technology.
7. Merlin Gerin Genie SF6 panels were last manufactured in 2003. (Merlin Gerin SF6 switchboards may have been installed and commissioned after this date and care should be taken to ensure the install/commission date is not inadvertently misread as the actual manufacturer date.)
Part A
1. This Safety Alert concerns all Merlin Gerin Genie SF6 switchboards.
2. The MMO, on direction from the DIO Regional Delivery Manager or Equivalent, shall initiate the following task:
  1. Establish all sites with Merlin Gerin Genie SF6 switchboards. (These will likely be in the ISS, SBSS, or other in door substations / switch rooms)
  2. Restrict access to sub-stations / switch rooms containing Merlin Gerin SF6 switchboards to essential personnel until the switchboard is confirmed to contain a satisfactory gas pressure by showing green in the sight glass/pressure gauge indicator. Exact access controls to be determined by the Authorising Engineer.
  3. Where a panel within a switchboard is identified as having low / no SF6 gas (gas pressure by showing red in the sight glass/pressure gauge indicator):
    1. The Authorising Engineer is to consider the need for the affected circuit breaker to remain in operation noting the potential effect on the system protection by the inhibited circuit breaker.
    2. Where the affected panel remains in operation it is to be dead operation only and a lock is to be fixed to the mechanical push button to prevent inadvertent operation. This operation restriction maybe lifted on completion of remediation and when the panel contains satisfactory gas pressure by showing green in the sight glass/pressure gauge.
3. The MMO is to notify the DIO Regional Delivery Safety Alerts Team (DIO-RDSafetyAlerts@mod.gov.uk) through their respective DIO Regional Delivery Manager identifying the location, quantity, date of manufacture, serial number (can be obtained from sticker as per example in Annex A) and whether the site glass for the SF6 is on green or red.

The requested data is required within 2 calendar months from issue date of this Safety Alert.

Part B
1. The MMO, on direction from the DIO Regional Delivery Manager or equivalent, shall initiate the following:
  1. For Merlin Gerin Genie SF6 switchboards with low / no gas pressure, contact the manufacturer’s representative Mr Keith Caygill, Technical Support Manager, (keith.caygill@se.com (07775 586 967) to arrange for remediation of the switchboard to be carried out.
  2. For Merlin Gerin Genie SF6 switchboards confirm during routine maintenance that the low / no gas pressure inhibit links are installed. Any found to be missing / modified are to be remediated to ensure the electrical interlock that prevents the electrical operation of the circuit breaker on low gas pressure is present.

The requirements at paragraph 15 should be conducted as part of the first 6 monthly maintenance task from the date of issue of this Safety Alert or at a period defined within the AE(E)’s Risk Assessment. i.e., all works should be conducted within a maximum period of 6 months but generally sooner. During this period access should be controlled and limited to essential personnel as detailed within Part A.

Part C
The MMO is to notify the DIO Regional Delivery Safety Alerts Team (DIO-RDSafetyAlerts@mod.gov.uk), through their respective DIO Regional Delivery Manager or equivalent, of the actions resulting from implementing the actions in Part B, Paragraphs 15 when completed.
Annex: A
Photographs
Photograph – 01: Genie SF6 failure on low gas

Photograph – 02: Label on back of switchboard showing serial number, date etc.