Safety Alert Parts A, B, & C				Health and Safety
Subject: Lubrication of HV and LV Circuit Breakers / Number: SA 2021-09
DIO Sponsor: Bryan Dunn			Date of issue: 20th December 2021
Contact if different from above Sponsor: / Stephen Bayliss / Technical Services, Engineering & Construction / Defence Infrastructure Organisation. / DMS Whittington, Lichfield. Staffordshire. WS14 9PY / Email: stephen.bayliss103@mod.gov.uk / Tel: +44 (0) 7971 708425
This Safety Alert is to be read by the following so appropriate action can be taken: / DIO’s Maintenance Management Organisations and their Supply Chains / DIO Regional Delivery Manager (or equivalent for non-NGEC contracts) / Head of Establishments / Others / Others interested in the content of this Safety Alert might include: / Assurance Managers, Estate Facility Managers, Assurance Managers in Regional (Service) Delivery Health & Safety Advisors, Top Level Budget Holders, Prime Contractors, Project Managers, Infrastructure Managers and Property Managers with responsibility for MOD projects and Property Management Works Services (including the legacy work of EWCs/WSMs), Authorised Persons (Electrical), Authorising Engineer (Electrical) etc.
When it takes effect: Immediately		When it is due to expire: When updated or rescinded.
	This Safety Alert does not necessarily cover all aspects of the subject matter and readers should make themselves aware of other potential issues. Readers should also not rely on DIO Publications as their only means of becoming aware of safety issues, but they should consult widely across other media to maintain awareness.

Aims
The aim of this Safety Alert is to bring to the attention of appropriate persons or organisations the correct maintenance requirements associated with lubrication of circuit breakers as part of the Maintenance Management Organisations’ (MMO) PPM Schedule and Tasks.
Introduction
1. Compliance with the contents of this Safety Alert will enable compliance with the Health & Safety at Work etc. Act 1974 and Electricity at Work Regulations 1989.
2. Any work required as a result of this Safety Alert must be carried out in accordance with the Management of Health & Safety in Ministry of Defence - JSP375.
Background
1. An investigation by the Health and Safety Executive (HSE) into an explosion of a high voltage circuit breaker indicated that recently carried out maintenance may have been a causal factor. The incident resulted in catastrophic failure of the HV circuit breaker leading to a fire/explosion and could have resulted in fatal injuries.
2. Maintenance of high voltage (HV) and low voltage (LV) circuit breakers typically involves both the cleaning and lubricating of the operating mechanism. The HSE investigation found that the same product was used for both maintenance activities, but evidence shows that the product was only suitable for cleaning and not lubrication. It is essential that the correct product is used for each task.
3. Further information can be found at the HSE’s safety notice: https://www.hse.gov.uk/safetybulletins/lubrication-circuit-breakers.htm
Part A
1. This Safety Alert concerns all HV and LV circuit breakers (excluding LV MCCB's and MCB's).
2. The Management Maintenance Organisation (MMO), on direction from the DIO Regional Delivery Manager (RDM) or equivalent, shall initiate the following tasks:
  1. Establish all sites with HV and LV circuit breakers (excluding LV MCCB's and MCB's)
  2. Provide assurance to the DIO RDM or equivalent that the cleaning and lubrication of the HV and LV circuit breakers has been carried out satisfactory, namely at the prescribed time intervals and using suitable cleaning and lubrication products as recommended by the manufacturer’s instructions.
  3. In particular, the maintenance procedure should ensure that the manufacturer’s instructions on cleaning and lubrication of the circuit breaker mechanism are followed at appropriate intervals, including the selection and application of the correctly specified lubricants (products) for the task. Where the specified products are no longer available appropriate and approved alternatives should be used.

The MMO is to notify the DIO Regional Delivery Safety Alerts Team (DIO-RDSafetyAlerts@mod.gov.uk) through their respective DIO Regional Delivery Manager identifying the type, location, quantity, date of manufacture and that the maintenance in relation to cleaning and lubrication of HV and LV circuit breakers has been conducted satisfactory.

The requested data is required within 2 calendar months the from issue date of this Safety Alert.

Part B
1. Where the MMO cannot provide the required assurance that the maintenance has been conducted satisfactory, as detailed within this Safety Alert, and on direction from the DIO Regional Delivery Manager or equivalent, shall initiate the following:
  1. The Authorising Engineer (Electrical) to conduct a risk assessment to assess whether the electrical equipment is safe for continued use or an Operational Restriction is necessary to control the danger.
  2. The maintenance of the electrical equipment, in relation to the cleaning and lubrication of the circuit breakers, shall be redone to the correct standard to provide the assurance required within this Safety Alert.

The requirements at paragraph 11 should be conducted as soon as practicable, but no longer than 6 months from the date of issue of this Safety Alert, or at a period defined within the AE(E)’s Risk Assessment.

Part C
The MMO is to notify the DIO Regional Delivery Safety Alerts Team (DIO-RDSafetyAlerts@mod.gov.uk), through their respective DIO Regional Delivery Manager or equivalent, of the actions, if any, resulting from implementing the actions in Part B, Paragraphs 11 when completed.
References.
1. The following documents provide further information on the maintenance requirements for HV and LV switchgear:
  1. HSE HSG 230 Keeping electrical switchgear safe
  2. BS6423:2014 - Code of practice for maintenance of low-voltage switchgear and control gear,
  3. BS6626:2010 - Maintenance of electrical switchgear and controlgear for voltages above 1 kV and up to and including 36 kV, and
  4. As prescribed in the manufacturer's instructions.