Safety Alert Parts A, B, & C				Health and Safety
Subject: Electrical Explosion in an Airfield Apron Floodlighting Control Box / Number: SA 2022/01
DIO Sponsor: Bryan Dunn			Date of issue: 20 Jan 2022
Contact if different from above Sponsor: / Khem Basel / Senior Electrical Engineer, Electrical Infrastructure Team, Technical Services, Engineering & Construction, Defence Infrastructure Organisation. / DMS Whittington, Lichfield. Staffordshire. WS14 9PY / Email: khem.basel539@mod.gov.uk / Tel: +44 (0) 7970 227690
This Safety Alert is to be read by the following so appropriate action can be taken: / DIO’s Maintenance Management Organisations (MMOs), their Supply Chain Staff including Authorised Engineers (Electrical), and Airfield Technicians / DIO Regional Delivery Manager (or equivalent for non-NGEC and overseas contracts) / Head of Establishments / Others / Others interested in the content of this Safety Alert might include: / Aerodrome Operators, Assurance Managers, Health & Safety Advisors, Top Level Budget Holders, Prime Contractors, Project Managers, Infrastructure Managers and Property Managers with responsibility for MOD projects and Property Management Works Services (including the legacy work of EWCs/WSMs) etc.
When it takes effect: Immediately		When it is due to expire: When updated or rescinded.
	This Safety Alert does not necessarily cover all aspects of the subject matter and readers should make themselves aware of other potential issues. Readers should also not rely on DIO Publications as their only means of becoming aware of safety issues, but they should consult widely across other media to maintain awareness.

Aim
1. The aim of this Safety Alert is to bring the attention of appropriate persons or organisations:
  1. An incident that occurred involving the explosion of apron floodlighting electrical components that could have result a serious injury and / or damage to aircraft.
  2. The failure to inspect and maintain floodlighting electrical systems, including luminaires and associated control equipment installed on MOD Establishments due to the assets not being included in the Establishment’s asset register and MMO’s maintenance schedule; and / or due to inconvenient access for inspection and maintenance.
  3. The requirement to identify where the lack of inspection and maintenance on the floodlighting electrical system exists and bring it to the attention of the appropriate persons.

Introduction
1. Compliance with the contents of this Safety Alert will enable compliance with the Health & Safety at Work etc. Act 1974, Electricity at Work Regulations 1989, and MAA Regulation 3590 (7).
2. On MOD Establishments occupied by United States Visiting Forces (USVF) responsibility is jointly held by USVF and DIO(USF). At base level this jointly managed organisation is to take appropriate action to implement the contents of this Safety Alert. Where this Alert contains procedures, which differ significantly from USVF practice, DIO(USF) code of practice will be issued.
3. Any work required as a result of this Safety Alert must be carried out in accordance with the Management of Health & Safety in Ministry of Defence – JSP 375.

Background
1. At approximately 2230 hrs. on Wednesday 5 May 2021, a loud explosion was heard which appeared to emanate from an apron on a MOD Airfield. Later, a large metal cover was found on a regularly used walkway, its dimensions were 350mm x 250mm x 150mm and weighted 4Kg. It was confirmed the metal cover had separated from the top of the floodlighting stanchion (over 25m height) immediately adjacent to the hangar and the apron.
2. Whilst the likelihood of the cover striking a person or an aircraft in this instance was considered to be low, the consequences could have been catastrophic. Had it hit a person or an aircraft it would have the potential to cause serious injury or damage. Accordingly, the incident was classified as a RIDDOR incident.

The investigation suggested:

  1. The floodlighting luminaire and its control box were beyond its service life. There was no evidence to confirm the asset was regularly inspected or maintained by a competent person since its installation approximately 30 years ago. It was suggested there had been a previous failure in the control box and it appeared the sealant on the metal cover was not re-applied correctly.
  2. The most probable cause of the incident was an incorrect seal allowed water ingress into the control box which caused an electrical short circuit on the conducting parts within the control box. Recovery of metal cover evidenced distortion and scorching consistent with electrical explosion in the floodlighting control box. There were also signs of scorching around the transformer which suggested the electrical short-circuit was the most probable cause of the explosion. The electrical protection system functioned correctly and disconnected the electrical supply.
2. Access to the floodlighting luminaires and their associated control equipment mounted at high level on stanchions may not always be convenient and this may have been a contributory factor.
3. Floodlighting luminaires and their associated control equipment of a similar age to that which exploded are likely to be present at MOD Establishments and may also have similar deficiencies in their maintenance and / or repair. Therefore, there is a potential for a similar incident to occur elsewhere.
4. A Defence Air Safety Occurrence Report (DASOR – Ref AHF \ 4 AAC \ No Aircraft \ 21 \ 4480) has been issued.

Part A
1. This Safety Alert concerns the condition of electrical systems (incl. luminaires and associated components) of all floodlighting on MOD Establishments.
2. The MMOs, on direction from the DIO Regional Delivery Manager (RDM) or equivalent shall initiate the following tasks:
  1. Establish all establishments with floodlighting systems.
  2. Provide assurance to the DIO RDM or equivalent that:
    1. maintenance of the floodlighting electrical systems has been satisfactorily completed and the installation is safe to continue in service, or
    2. identify where floodlighting electrical systems are:
      1. not recorded in the Asset Register for periodic inspection and maintenance; and / or
      2. not adequately inspected or maintained and their condition is unknown.
  3. Until assurance can be provided suitable and sufficient measures are to be put in place to protect persons, equipment, aircraft, etc. in the vicinity of the identified floodlighting equipment.

1. The MMO is to notify the DIO Regional Delivery Safety Alerts Team (DIO-RDSafetyAlerts@mod.gov.uk) through their respective DIO Regional Delivery Manager identifying the type, location, & quantity, and that the maintenance of the floodlighting luminaires has been satisfactorily completed in the required time interval
2. The requested data is required within 3 calendar months from issue date of this Safety Alert. A nil return is required from establishments with no floodlighting on aircraft aprons or similar areas used by aircraft.

Part B
1. Where the MMO is unable to provide the required assurance that the maintenance of the floodlighting electrical system has been conducted satisfactorily, as detailed within this Safety Alert, and on direction from the DIO Regional Delivery Manager or equivalent, shall initiate the following:
  1. Undertake an inspection of the floodlighting electrical system (incl. luminaires and associated components) by a competent person to determine its condition and where necessary identify repair or replacement works for its continued safe operation.
(Particular emphasis should be placed on electro-mechanical integrity, secureness, and wear & tear due to adverse environmental effects on the luminaires, associated components, and installation.)
  1. Determine if the inspection at para 15a may be carried out in conjunction with existing planned maintenance tasks e.g., HFMST110, 228, 231, & 234.
  2. Notify the DIO EFM of the outcomes of the Inspection at para 15a.
  3. Where floodlighting systems have not been maintained ensure their future maintenance is to be included in the Establishment’s maintenance regime.
  4. Document all actions resulting from implementing instructions at para 15. This document shall be made available for a review during the next Biennial Airfield Inspection or an ad-hoc Inspection from DIO Technical Services.
2. A suitable and sufficient risk assessment shall be carried out regarding floodlighting electrical systems where maintenance or safety cannot be assured, and the required inspection and maintenance be undertaken as soon as practicable.
Part C
The MMO is to notify the DIO Regional Delivery Safety Alerts Team (DIO-RDSafetyAlerts@mod.gov.uk); through their respective DIO Regional Delivery Manager or equivalent of the actions, if any, resulting from implementing the instructions in paragraph 15 when completed.

Annex: A
Photographs
Photograph -1: Floodlighting installation	Photograph -2: Control box (yellow circle)

Photograph -3: Luminaire control box cover	Photograph -4: Internal parts of the control box

Photograph -5: Luminaire control box cover	Photograph -6: Signs of electrical burn and explosion

Photograph -7: Luminaire control box and cover	Photograph -8: General condition of internal parts

Photograph -9: General condition of internal parts	Photograph -10: General condition of internal parts