## Sheet1
Radon Gas Management Guidance - Outcomes & Responsibilities Version 1.1
Required Outcomes | Actions | Accountability | Lead Responsibility | Responsibility Support
Desktop Survey Each affected property must be assessed to ascertain if a Radon Survey is required. | Complete an indicative survey for each affected property minimum every 3 years using UK Radon website. Using the UK Radon website, check to see if the site or any part of it, is within a 1 km grid square of a Radon Affected Area (RAA) and meets the criteria to be considered in a radon affected area. | PCT | MoJ PS | MoJ PS - Carry out initial review for affected properties using the UK Radon website and log results as evidence. The information should be logged in CAFM under the relevant Radon PM for each site. An overview of all properties by Service Provider will also be issued to them via CEMAR.
| Complete a geological survey every 10 yeas as a minimum. | RPOM | MoJ PS | MoJ PS - carry out a geological survey
| Whether in a Radon Affected Area (RAA) or not, confirmation is required to see if the site has any subterranean rooms and basements. | APOM | MoJ PS | MoJ PS - Confirm with the FM Provider to confirm if there are any subterrnean rooms at the site and ensure the locations are identified in the CAFM Drawing Schedules.
|  | FM Provider | FM Provider | FM Provider - to support MoJ PS to confirm subterranean rooms (and other Radon affected rooms) and log the locations in the CAFM Drawing schedules.
Register of all rooms with subterranean rooms identified (CAFM Drawing Schedules) A register of all rooms including subterranean rooms must be kept. | A register of all rooms with subterranean rooms identified must be maintained, which includes an evaluation of the duration of occupancy for each area. The register must identify and include the responsibility owner. | FM Provider | FM Provider
|  | APOM | MoJ PS | MoJ PS - are to ensure that FM provider has a register of all rooms including subterranean rooms. This will be used to determine frequency of PPMs and risks to occupants.
|  | Governor | HMPPS | HMPPS to provide information on occupancy to FM Providers.
| The register must be reviewed when a change of use occurs or at least annually. | FM Provider | FM Provider | FM Provider - review the Radon room register to ensure this is updated and maintained and aligned with the CAFM system.
Survey Monitoring & Report Sample monitoring is carried to ascertain the levels of Radon Gas. This work must be carried out by a Radon specialist contractor and all findings recorded in accordance with BS8576, L121 'Work with Radiation' and IR regulations. A report must be provided. Radon managment on site must be dicussed at the tripartite meetings. | Where subterranean rooms are used for more than 50 hours and whether in a radon area or not, radon monitoring must be completed and report provided. | FM Provider | FM Provider | FM Provider - must ensure radon monitoring is carried out by a Radon specialist contractor. The monitoring should be carried out over a 3 month period. The results will be presented in a report. FM RPA must provide advice on temporary mitigations as soon as an action level has been reached. Any levels reported above the guidance threshold must be immediately escalated to HMPPS RPA, LOCAL SHSFA, PHSFA, APOM, RPOM and Governor/Director
| Where there is evidence of readings in excess of 200 Bq/m3 in living accommodation or 300 Bq/m3 in other work rooms. The outcomes of the report must be reported to the HMPPS RPA, LOCAL SHSFA, PHSFA, APOM, RPOM and Governor/Director | FM Provider | FM Provider
| Where there is evidence of readings in excess of 200 Bq/m3 in living accommodation or 300 Bq/m3 in other work rooms. As the employer HMPPS must notify the HSE | HS&F | HMPPS | HMPPS - will engage the services of their RPA on receipt of information confirming that levels are above action levels. HMPPS will be responsible for reporting the above action levels to the HSE & UKHSA
Radon Risk Assessment (RA) Where exposure is present, the FM provider must put in place a Radon risk assessment (completed by a competent person) and in accordance with L121 'Work with Radiation' and IR Regulations. A risk assessment of exposure is to be made and documented for each establishment or site in respect of those affected. This should outline the controls and monitoring in place to maintain levels below the statutory action levels. The International Commission on Radiological Protection (ICRP) Publication number that has been used must be included in the RA documentation. | A Radon risk assessment must be in place for the affected site and outline the controls and monitoring in place to maintain levels well below the statutory action levels. The Radon risk assessment for the site must be shared with the prison HSF Committee annually or more frequently where there is a change in the assessment. | FM RPA | FM Provider | FM Provider - The FM Provider's RPA must complete the Radon risk assessment. The ICRP Publication number that has been used must be included in the RA documentation. The completed RA must be shared with MOJ PS and HMPPS RPA, LOCAL SHSFA, PHSFA, APOM, RPOM and Governor/Director. (Director applies to Private Sector Prisons) A Radon Management update must be presented to the prison HSF Committee at least annually. HMPPS & MoJ will work with FM provider to ensure they have all relevant information required to complete the risk assessment.
| Where staff are exposed to level of Radon in excess of the limits, an exposure assessment for individuals must be carried out and shared. | HMPPS RPA | HMPPS | HMPPS - Carried out an exposure assessment for their employees other individuals on site affected by HMPPS' undertakings (including FM providers staff or FM providers sub contractors). HMPPS will be responsible for informing the above action level exposure of third party employees to their employer
Mitigation Survey & Monitoring Where readings from the survey monitoring is above action levels (readings in excess of 200 Bq/m3 in living accommodation or 300 Bq/m3 in other work rooms). A mitigation survey must be carried out by a Radon Specialist contractor, and include radon testing and formal recommendations for any remedial works. | Where readings are above action levels. A mitigation survey must be completed by an accredited Radon specialist contractor which should include radon testing and formal recommendations for any remedial works required. | FM Provider | FM Provider | FM Provider - to ensure a mitigation survey is carried out by an accredited radon Specialist contractor. Agreed mitigations will be shared with HMPPS, Governor, and HMPPS RPA FM Provider is not responsible for funding associated Radon mitigation works
| The outcomes of the mitigation survey must be shared at the earliest opportunity with Local SHSFA, PHSFA, APOM, RPOM and Governor/Director. | FM Provider | FM Provider | FM Provider - must share the outcomes of the mitigation survey at the earliest opportunity with MoJ PS, HMPPS RPA, LOCAL SHSFA, PHSFA, APOM, RPOM and Governor/Director . HMPPS will be responsible for assessing residual risks and implement a contingency plan (ie local control measures)
| Operational management checks must be completed to ensure mitigation controls are in place on a quarterly basis. People on site must abide by local rules and not tamper with controls that are in place. e.g. vents must remain clear from obstruction and unblocked | HS&F | HMPPS | HMPPS - to ensure operational management checks are taking place and evidenced.
| Action must be taken to check any mitigation is working correctly to restrict exposure levels. | HS&F | HMPPS | HMPPS - to monitor operational management mitigations are working effectively regarding the establishment operational management issues. HMPPS will share by exception (ie where an issue is identified)
| Action must be taken to check any mitigation is working correctly to restrict exposure levels. | FM RPA | FM Provider | FM Provider - to monitor mitigation is working effectively regarding mechanical built environment issues. e.g. check to ensure pumps or fans are still working, etc. and rectify issues that are identified. Escallate issues where they cannot be immediately resolved.
Radiation Protection Adviser (RPA) Professional advice must be obtained from the FM providers RPA to inform the mitigation survey they commission and the subsequent recommendations. The FM providers RPA must liaise with the HMPPS RPA and keep them fully informed of the Radon levels, the proposed mitigations and the ongoing monitoring. | The outcomes of the mitigation survey and recommendations must be discussed and agreed with the FM appointed RPA and actioned. The HMPPS RPA must be kept informed of site related Radon issues and proposed mitigations. | HS&F | HMPPS | HMPPS RPA, LOCAL SHSFA, PHSFA, APOM, RPOM, FM Provider and Governor/Director - to discuss and agree outcomes of the mitigation survey regarding the operational management issues. E.g. ensuring air bricks remain uncovered. HMPPS will share by exception (ie where an issue is identified)
|  | FM Provider | FM Provider | FM Provider, Specialist Contractor and FM Appointed RPA - to discuss and agree outcomes of the mitigation survey regarding mechanical built environment issues. e.g. check to ensure pumps or fans are still working. FM Provider is not responsible for funding associated Radon mitigation works
| Where readings are above the action level, temporary mitigations and local rules must be put in place on the advice of the FM appointed RPA. (Local rules are required whilst above action levels, once work completed to mitigate levels to reduced levels local rules will no longer be required). Whilst local rules are in place HMMPS must appoint an RPS. | HS&F | HMPPS | HMPPS - temporary mitigations and local rules must be put in place on the advice of the FM appointed RPA regarding the operational management issues. HMPPS RPA to be kept informed of mitigations proposed and put in place. HMPPS appointed RPS to oversee the management and implementaiton of the local rules. HMPPS will be responsible for assessing residual risks and implement a contingency plan (ie local control measures)
|  | FM Provider | FM Provider | FM Provider - temporary maintainable M&E mitigations and local rules must be put in place on the advice of their appointed RPA regarding the built environment issues. FM Provider is not responsible for funding associated Radon mitigation works
Communications & Training Provision of information, instruction and training must be made available to the workforce. | Staff must be provided with Radon information, instruction, and training as appropriate for each site i.e. What radon is; How it occurs; Hazard presented - increased risk of cancer. Locally where in a radon area, required not to tamper or alter any controls (such as vents being blocked) Understand meaning of signs used for controlled areas. | HS&F | HMPPS | HMPPS - to provide all staff, prisoners, contractors & visitors with Radon Information and training as appropriate for each site on the advice of their RPA. FM Provider to ensure visitors/staff/sub-contractors are aware of management plan
CAFM System A planned maintenance regime must be in place within the CAFM system. Inspections must be carrioed out 12 monthly as a minimum or otherwise directed by the risk assessment in high-risk areas. Records must be maintained and available as evidence. | There must be a PPM on CAFM in accordance with SFG 20 88-47 and the risk assessment, which is planned in and records must be available and shared with local SHSFA, PHSFA, APOM, RPOM and Governor/Director. | FM Provider | FM Provider | FM Provider - to manage Radon related PPM and remedials effectively within the CAFM systems. Ensuring Work Orders are updated, completed and closed appropriately. MoJ PS - to ensure that CAFM planned maintenance is established and remains up to date and FM providers are delivering against their commitments.
| Remedial actions must be identified and completed at the earliest opportunity | FM Provider | FM Provider | FM Provider - The work must be completed and closed appropriately in the CAFM system.
| Any re-assessment of Radon levels requirements set out in the report must be planned into the CAFM system. | FM Provider | FM Provider | MOJ PS - ensure reassessment requirements are captured in CAFM. FM Provider - to re-assess Radon levels to validate mitigation has been effective.