Project’s Information Standard

Employer’s requirements

Project code: [SRP/FS/FE code]

Project name: [Name of school/college]

[Month] 20[XX]

Contents

Summary	5

Review date	5

Who this publication is for?	5

Document history	7

Template	7

Project specific	7

Abbreviations	8

References	12

1 Introduction	13

1.1 DfE Construction Framework 2025	13

2 Standards	14

2.1 Information management standards	14

2.2 Specific standards	15

2.2.1 Abbreviations	15

2.2.2 Construction tolerances	15

2.2.3 Documents	16

2.2.4 Drawing content	17

2.2.5 Drawing sheet sizes	17

2.2.6 Drawing scales	17

2.2.7 Units and measurement	18

2.2.8 Annotation and text for drawings	19

2.2.9 Dimensions	19

2.2.10 Date and time numbering	19

2.2.11 Coordinates	20

2.2.12 Levels	20

2.2.13 Symbols	20

3 Exchange of information	22

3.1 Exchange formats	22

4 Structuring and classifying information	24

4.1 IFC (Industry Foundation Classes)	24

4.1.1 All IFC-SPF	24

4.1.2 IFC-SPF for COBie generation	24

4.1.3 Acceptable alternative IFC-SPF to COBie workflows	25

4.2 COBie (Construction Operations Building information exchange)	25

4.3 COBie Quality Control (QC) Report	27

4.4 Native drawings	28

4.5 Classification and categorisation	28

4.5.1 Asset classification	28

4.5.2 Costing classification	30

4.6 Layer requirements	30

4.6.1 Layer format	30

4.6.2 Agent	30

4.6.3 Element	30

4.6.4 Presentation	31

4.6.5 Description	31

4.6.6 Example layers	31

5 Nomenclature	32

5.1 File naming, revisions and status	32

5.1.1 File naming format	32

5.1.2 Project code	33

5.1.3 Originator codes	33

5.1.4 Functional breakdown codes	35

5.1.5 Spatial breakdown codes	36

5.1.6 Form codes	37

5.1.7 Discipline codes	37

5.1.8 Number codes	39

5.1.9 Status and revision codes	39

5.1.10 File naming examples	41

5.1.11 Information container structures	42

5.2 Standardised values	42

5.2.1 Project nomenclature	42

5.2.2 Site nomenclature	43

5.2.3 Building(s) nomenclature	43

5.2.4 Building storey (Floor) nomenclature	44

5.2.5 Space nomenclature	45

5.2.6 Zone nomenclature	46

5.2.7 Object nomenclature – Type	48

5.2.8 Object nomenclature – Occurrence	49

5.2.9 System nomenclature	77

5.2.10 COBie picklists	89

6 Common data environment	93

6.1 Information sharing at tender phase	93

6.2 Project’s common data environment	93

6.3 Distributed common data environments	94

7 Security-minded approach	96

7.1 Outcome of the security triage process	96

7.2 Security of information generally	96

7.3 Disclosure of information	97

7.4 Security-minded approach	97

8 Method of assignment for level of information need	98

9 Use of information during the operational phase of the asset	99

Appendix A – Operation and Maintenance (O&M) Manual structure	100

Volume 1: Introduction and key information	100

Volume 2: Building Elements	101

Volume 3: Building Services	102

Volume 4: Site and Infrastructure	103

Appendix B – Health and Safety File structure	104

Appendix C – Building Log Book Structure	106

Appendix D – Building User Guide Structure	107

# Summary

This document is the Project’s Information Standard for use on all DfE delivered schemes using the DfE Construction Framework 2025 (CF25). The completed Project’s Information Standard forms part of the DfE’s information management requirements for schemes and shall be read in conjunction with:

Project’s Information Protocol

Exchange Information Requirements

Detailed Exchange Information Requirements

Project’s Information Production Methods and Procedures

Advisory note

This document contains a series of advisory notes that should be deleted once addressed by the Technical Advisor, including this one.

## Review date

This document shall normally be reviewed at 12-month intervals however, DfE reserve the right to update it at any time.

## Who this publication is for?

This resource is for:

local authorities (for community, voluntary-controlled schools, foundation schools and maintained nursery schools)

academy trusts (for academies and free schools)

governing bodies (for voluntary-aided schools)

school/college leaders, staff and governing bodies in; further education colleges and designated institutions, sixth form colleges, maintained schools, academies and free schools, pupil referral units, City Technology Colleges, non-maintained special schools and maintained nursery schools

technical professionals involved in the design, construction and maintenance of school and college premises.

Academy trusts with a religious character and the responsible bodies for voluntary-aided and voluntary controlled schools should engage with the land/site trustees for their land and buildings and the relevant religious body, most often their Diocese.

## Document history

This table lists the key changes in each update

### Template

| Revision code | Status code | Date | Amendment |
| --- | --- | --- | --- |
| C01 | A | 2026-01-12 | GOV.UK publication |

### Project specific

| Revision code | Status code | Date | Amendment |
| --- | --- | --- | --- |
| Pnn | Sn | 20YY-MM-DD | Employer's Representative to add amendments made to document here and rename file to make project specific |

The DfE and its agents and advisers accept no liability whatsoever for any expense, liability, loss, claim or proceedings arising from reliance placed upon this resource.

# Abbreviations

In the context of DfE’s information management requirements, the following abbreviations shall have the meanings given to them below:

Ac: Activities (Uniclass Ac Classification)

ADSL: Asymmetric Digital Subscriber Line

AFFL: Above Finished Floor Level

AIM: Asset Information Model

AIR: Asset Information Requirements

BEP: BIM Execution Plan

BIM: Building Information Modelling

BMS: Building Management System

BPSS: (UK Government) Baseline Personnel Security Standard

BSI: British Standards Institute

CAFM: Computer Aided Facilities Management

CCP: Certified Cyber Professional

CCS: Crown Commercial Services

CCSC: Certified Cyber Security Consultant

CDD: Contractor’s Design Documents

CDE: Common Data Environment

CDM: Construction (Design and Management)

CEM: Client Engagement Meeting

CF25: DfE Construction Framework 2025

Co: Complexes (Uniclass Co Classification)

COBie: Construction Operations Building information exchange

CoW: Clerk of Works

CP: Contractor’s Proposals

CV: Curriculum Vitae

D&B: Design and Build

DA: Design Advisor

DEIR: Detailed Exchange Information Requirements

DfE: Department for Education

DSP: Design Submission Procedure

DWG: Drawing File

EF: Elements/ functions (Uniclass EF Classification)

EIR: Exchange Information Requirements

En: Entities (Uniclass En Classification)

EoI: Expression of Interest

ER: Employer’s Requirements

EW: Early Works

FBC: Final Business Case

FF&E/FFE: Fittings, Furniture and Equipment

FFL: Finished Floor Level

FI: Form of Information (Uniclass FI Classification)

FM: Facilities Management

FS: Free School

FSC: Free Schools Capital

GEMS: Good Estates Management Strategy

GIA: Gross Internal Area

GIFA: Gross Internal Floor Area

GSC/GSCP: Government Security Classification/Government Security Classification Policy

GSL: Government Soft Landings

H&S: Health and Safety

HMG: His Majesty’s Government

HSQW: Health, Safety, Quality and Workmanship

HVB: High Value Band

ETA: Education Technology Advisor

ICT: Information and Communications Technology

IFC: Industry Foundation Classes (i.e., the schema)

IFC-SPF: Industry Foundation Classes Step Physical File (i.e., the file format)

ISO: International Standards Organisation

ISP: Invitation to Submit Proposal or Internet Service Provider

ITT: Invitation to Tender

ICWI: The Institute of Clerks of Works and Construction Inspectorate

KPI: Key Performance Indicator

LCC: Legal Counsel Construction

LCR: Legal Counsel (Real Estate)

LVB: Low Value Band

Ma: Materials (Uniclass Ma Classification)

MEP: Mechanical, Electrical and Public Health (also known as Building Services)

MIDP: Master Information Delivery Plan

MIR: Management Information Requirements

MVD: Model View Definition

NBS: National Building Specification

NC: Non-Conformance

NCSC: National Cyber Security Centre

O&M: Operation and Maintenance

OBC: Outline Business Case

OIR: Organisational Information Requirements

PBDA: Performance Based Direct Allocation

PC: Properties and characteristics (Uniclass PC Classification)

PCSA: Pre-Construction Services Agreement

PD: Project Director

PDF: Portable Document Format

PIM: Project Information Model

PITT: Preliminary Invitation to Tender

PoW: Plan of Work

PM: Project Manager/Project Management (Uniclass PM Classification)

Pr: Products (Uniclass Pr Classification)

PrinD: Principal Designer

PSBP: Priority School Building Programme

QC: Quality Control

RAG: Red, Amber, Green

RB: Responsible Body

RBAC: Role Based Access Control

RDD: Reviewable Design Data (term formally used for CDD: Contractor’s Design Documents)

RFI: Request For Information

RIBA: Royal Institute of British Architects

RICS: Royal Institute of Chartered Surveyors

RIDDOR: Reporting of Injuries, Diseases and Dangerous Occurrences Regulations

RK: Risk (Uniclass RK Classification)

Ro: Roles (Uniclass Ro Classification)

RSoW: Refurbishment Scope of Works

SEM: Stakeholder Engagement Meeting

SGR: Suitability Gateway Review

SIRA: Senior Information Risk Advisor

SIRO: Senior Information Risk Owner

SL: Spaces/ locations (Uniclass SL Classification) or Soft Landings

SoA/SOA: Schedule of Accommodation

SoS: Secretary of State

SPM: Selected Panel Member (referred to as Contractor)

SRP: School Rebuilding Programme

Ss: Systems (Uniclass Ss Classification)

TA: Technical Advisor

TCA: Technical and Cost Advisor

TE: Tools and equipment (Uniclass TE Classification)

TIDP: Task Information Delivery Plan

TPD: Technical Product Documentation

UAT: User Acceptance Testing

UPRN: Unique Property Reference Number

USB: Universal Serial Bus

Zz: CAD (Uniclass Zz Classification)

## References

A number of documents and files, in whole or in part, are referenced in this resource. Where a date is referenced, the edition cited applies. Where a date is not referenced the latest edition of the referenced resource, document or file (including any amendments) applies.

# 1 Introduction

DfE have established the specific information standards required by the DfE organisation within this Project’s Information Standard.

In doing this, DfE have considered:

- relevant standards, specifications and guidance

- the exchange of information

- the means of structuring and classifying information

- nomenclature

- the use of a common data environment

- the method of assignment for level of information need, and

- the use of information during the operational phase of the asset

This resource satisfies the requirements of BS EN ISO 19650-2 clause 5.1.4.

## 1.1 DfE Construction Framework 2025

Refer to the DfE’s Exchange Information Requirements for more information regarding the DfE Construction Framework 2025.

With regard to this resource, all sections in this resource apply to all lots and both value bands of the DfE Construction Framework 2025.

# 2 Standards

## 2.1 Information management standards

The following are standards that shall be applied on this project.

| Name | Description |
| --- | --- |
| BS EN ISO 13567-2:2017 | Technical product documentation. Organization and naming of layers for CAD - Concepts, format and codes used in construction documentation |
| BS EN ISO 19650-1:2018 | Organization and digitization of information about buildings and civil engineering works, including building information modelling (BIM). Information management using building information modelling - Concepts and principles |
| BS EN ISO 19650-2:2018 & Revised NA | Organization and digitization of information about buildings and civil engineering works, including building information modelling (BIM). Information management using building information modelling -Delivery phase of the assets |
| BS EN ISO 19650-4:2022 | Organization and digitization of information about buildings and civil engineering works, including building information modelling (BIM). Information management using building information modelling - Information exchange |
| BS EN ISO 19650-5:2020 | Organization and digitization of information about buildings and civil engineering works, including building information modelling (BIM). Information management using building information modelling - Security-minded approach to information management |
| BS EN ISO 12006-2:2020 | Building construction. Organization of information about construction works - Framework for classification |
| PAS/ISO 16739:2005 | Industry Foundation Classes (IFC) for data sharing in the construction and facility management industries (IFC2x3 TC1) |
| BS ISO 19005-1:2005 | Document management. Electronic document file format for long-term preservation - Use of PDF 1.4 (PDF/A-1) |
| BS ISO 8601-1:2019+A1:2022 / BS ISO 8601-2:2019 | Date and time. Representations for information interchange - Basic rules; and - Extensions |
| BS EN ISO 7817-1:2024 | Building Information Modelling. Level of Information Need - Concepts and principles |

Post-handover, the asset will be expected to align with processes set out in BS EN ISO 19650-3:2020 ‘Organization and digitization of information about buildings and civil engineering works, including building information modelling (BIM). Information management using building information modelling - Operational phase of the assets’.

## 2.2 Specific standards

### 2.2.1 Abbreviations

The following abbreviations shall be used for this project.

| Name | Description |
| --- | --- |
| BS 1635:1990 | Recommendations for graphic symbols and abbreviations for fire protection drawings |

### 2.2.2 Construction tolerances

The following construction tolerances shall apply to this project.

| Name | Description |
| --- | --- |
| BS 5606:2022 | Accuracy and tolerance in design and construction. Guide |

### 2.2.3 Documents

In order to align with the guidance published on GOV.UK, Publishing accessible documents, all documents shall adhere to the following:

- file naming and revisions shall be as set out in 5.1 File Naming, revisions and status

- document descriptions shall be meaningful and match those documented in the Task/Master Information Delivery Plan and as provided on the project’s common data environment

- keep sentences and paragraphs short. Aim for around 25 words or less per sentence

- use a sans serif font like Arial or Helvetica. Arial is preferred. Use a minimum size of 12 points (smaller font sizes on documents will be rejected)

- use sentence case. Avoid all caps text and italics

- make sure the text is left aligned, not justified

- avoid underlining, except for links

- make sure link text clearly describes where the link goes. It should also be understandable on its own, even if read out of context. This is because some screen reader users list links on a page to find what they need quickly

- documents with single continuous columns of text are easier to make accessible than documents with a complex layout

- only use tables for data. Keep tables simple: avoid splitting or merging cells

- do not use things like colour or shape alone to show meaning. Instructions like ‘click the big green button’ rely on the user to see the page and someone who is colour blind may not see the green button

- if you’re using images or charts, think about how you’ll make the content accessible to people with a visual impairment. Two options are:

  - make the same point in the text of the document (so people with visual impairments get the information they need - the image or chart is there as an extra for people who are able to see it)

  - give the person converting or uploading the document for you alt text (‘alternative text’) for the image or chart

  - do not use images containing text, as it’s not possible to resize the text in the image and screen readers cannot read text which is part of an image

  - avoid footnotes where possible. Provide explanations inline instead

  - break up your document to make it more readable. Use bullet points, numbered steps and meaningful subheadings

  - do not use bold to mark up subheadings. Use styles to create a hierarchy of headings: ‘heading 1’, ‘heading 2’ and so on

  - use styles for tables and bullet lists. That way, a screen reader will recognise the formatting and read out the content correctly

### 2.2.4 Drawing content

Information content for drawings shall include the following as a minimum:

- file naming and revisions as set out in 5.1 File naming, revisions and status

- drawing descriptions shall be meaningful and match those documented in the Task/Master Information Delivery Plan and as provided on the project’s common data environment

- document descriptions shall use sentence case. Avoid all caps text and italics

- cross referencing to other drawings and documents

- labelled entities shall align with drawings and documents

- north points to all plan information

- scale bars

- standard notes, and

- where appropriate, Safety Health & Environment (SHE) boxes, hazard identification etc

### 2.2.5 Drawing sheet sizes

The following drawing sheet sizes in millimetres shall be used for this project.

| Sheet | Size |
| --- | --- |
| A0 | 1189 x 841 |
| A1 | 841 x 594 |
| A2 | 594 x 420 |
| A3 | 420 x 297 |
| A4 | 297 x 210 |

### 2.2.6 Drawing scales

All drawing templates shall be rendered and presented at one of the approved scales below. Scales other than those approved shall not be used. The templates shall also be in the standard format for sharing and interoperability.

| Scale | Description |
| --- | --- |
| 1:2500 | -- |
| 1:1250 | -- |
| 1:1000 | Shows shape and layout |
| 1:500 | -- |
| 1:200 | -- |
| 1:100 | Shows shape, layout and construction elements |
| 1:50 | Shows how construction elements meet at junctions |
| 1:20 | -- |
| 1:10 | -- |
| 1:5 | Shows shape, dimensions and assembly of the separate construction elements |
| 1:2 | Shows shape, dimensions and assembly of the separate construction elements |
| 1:1 | All model files shall be modelled at 1:1 scale |

### 2.2.7 Units and measurement

The following units of measurement shall be used for this project.

| Units/measurement | Requirement |
| --- | --- |
| Area measurement | squaremetres |
| Area units | squaremetres |
| Angles | degrees |
| Coordinate X Axis | millimetres |
| Coordinate Y Axis | millimetres |
| Coordinate Z Axis | millimetres |
| Currency Units | pounds |
| Elevation | millimetres |
| Gross Area | squaremetres |
| Height | millimetres |
| Linear Units | millimetres |
| Net Area | squaremetres |
| Nominal Height | millimetres |
| Nominal Length | millimetres |
| Nominal Width | millimetres |
| Replacement Cost | pounds |
| Time Units | years |
| Usable Height | millimetres |
| Volume Units | cubicmetres |
| Weight | kilograms |

The requirement is set out in the format aligned to the COBie schema i.e., no spaces in the text.

### 2.2.8 Annotation and text for drawings

The font type used shall be Arial unless otherwise noted.

Generally, the following shall be applied:

Text height (mm) – When plotted full size use

1.8 mm - General text, dimensions, notes

2.5 mm - General text, dimensions, notes

3.5 mm - Sub-headings

3.5 mm - General text, dimensions, notes – A0 drawings

5.0 mm - Normal titles, drawing numbers

7.0 mm - Major titles

Correct use of text size shall be used to ensure legibility of drawings when they are printed at reduced sizes including A3 record information.

### 2.2.9 Dimensions

All dimensions shall be in millimetres.

Dimension text shall be Arial unless otherwise noted.

### 2.2.10 Date and time numbering

Date and time numbering shall be as BS ISO 8601-1:2019+A1:2022 / BS ISO 8601-2:2019. The following conventions shall apply to this project.

| Field | Format |
| --- | --- |
| Year | YYYY e.g., 2026 |
| Year and month | YYYY-MM e.g., 2026-01 |
| Date | YYYY-MM-DD e.g., 2026-01-31 |
| Combined date and time | YYYY-MM-DDThh:mm:ss e.g., 2026-01-31T09:25:35 |

### 2.2.11 Coordinates

The coordinate system of the project shall be to UK Ordnance Survey.

All models shall be based on standard eastings and northings as displayed in the Ordinance Survey.

For the purposes of interoperability, particularly for IFC exchanges, the Origin (e.g., Internal, Project, and Survey as applicable) of each file shall match and be positioned in the same geographical location.

Regardless of the software platform, the files shall be orientated to True North and use the following coordinates to define the respective Project Origin.

| Field | Grid intersection | Northing | Easting |
| --- | --- | --- | --- |
| Software origin | OS Grid location | TBC | TBC |
| Grid intersection 1 | TBC | TBC | TBC |
| Grid intersection 2 | TBC | TBC | TBC |
| Grid intersection 3 | TBC | TBC | TBC |
| Grid intersection 4 | TBC | TBC | TBC |
| Angle to true north (clockwise from 3 o’clock) | n/a | n/a | TBC degrees |

### 2.2.12 Levels

Refer to 5.2.4 Building storey (Floor) nomenclature for levels.

### 2.2.13 Symbols

The following symbols shall be used for this project.

| Name | Description |
| --- | --- |
| BS 1635:1990 | Recommendations for graphic symbols and abbreviations for fire protection drawings |
| BS EN ISO 4172:2024 | Technical product documentation (TPD). Construction documentation. Drawings for the assembly of prefabricated structures |
| BS 5070-3:1988 | Engineering diagram drawing practice - Recommendations for mechanical/fluid flow diagrams |
| BS 5070-4:1990 | Engineering diagram drawing practice - Recommendations for logic diagrams |
| BS 8541-2:2011 | Library objects for architecture, engineering and construction - Recommended 2D symbols of building elements for use in building information modelling |
| BS EN ISO 8560:2019 | Technical drawings. Construction drawings. Representation of modular sizes, lines and grids |
| BS EN ISO 11091:1999 | Construction drawings. Landscape drawing practice |

# 3 Exchange of information

The exchange of information for this project has considered the following information exchanges:

within the DfE

between the DfE and external stakeholders

between the DfE and external operators or maintainers

between the DfE/Technical Advisor and the Contractor

between the prospective Contractor and the Technical Advisor/DfE

between prospective appointed parties on the same project, and

between interdependent projects

## 3.1 Exchange formats

The following are the agreed exchange formats between software solutions:

| File type | Export | Import | Format |
| --- | --- | --- | --- |
| COBie | All | n/a | XSLX |
| COBie QC Reporter | Software A | n/a | TBC |
| Document | All | n/a | PDF |
| Drawing | All | n/a | PDF |
| Model - Three dimensional | All | n/a | Native and IFC-SPF |
| - | Software A | Software A | TBC |
| - | Software A | Software B | TBC |
| - | Software B | Software B | TBC |
| - | Software B | Software C | TBC |
| Model – Two dimensional | All | n/a | DWG / DXF |
| - | Software A | Software B | TBC |
| Issues | Software A | Software D | BCF |
| - | Software B | Software D | BCF |
| - | Software C | Software D | BCF |
| Schedule | All | n/a | XSLX / PDF |
| Video/ Animations | All | n/a | MPEG |
| Visualisation | All | n/a | JPG |

# 4 Structuring and classifying information

This section sets out how information shall be structured for the project and which classifications shall be used.

## 4.1 IFC (Industry Foundation Classes)

The agreed information schema for this project is buildingSMART International's IFC2x3 TC1 schema (PAS/ISO 16739:2005).

### 4.1.1 All IFC-SPF

In order to exchange valid IFC-SPF the following shall be adhered to for all files as a minimum:

all file names shall be compliant with 5.1 File naming, revisions and status

all models shall meet the requirements of the Model View Definition (MVD) that they are being exported for

all model objects shall have their entity correctly defined. Where an entity is not available from standard entities then Building Element Proxy shall be used

each entity shall also have a correctly defined enumeration (predefined type). NOTDEFINED shall not be used. USERDEFINED shall be used where an appropriate predefined type cannot be found in the standard enumerations provided by the schema. IfcElementType shall be associated to each USERDEFINED type

all models shall have the following nomenclature provided as a minimum:

  - project name in accordance with information set out in 5.2.1 Project nomenclature

  - site name in accordance with information set out in 5.2.2 Site nomenclature

  - building name(s) in accordance with information set out in 5.2.3 Building(s) nomenclature

  - building storey (Floor) names in accordance with information set out in 5.2.4 Building storey (Floor) nomenclature

all IFC-SPF shall have layers that conform to the requirements set out in 4.6 Layer requirements

### 4.1.2 IFC-SPF for COBie generation

Where IFC-SPFs are used to generate COBie the following shall be adhered:

classification references in accordance with the requirements of 4.5 Classification and categorisation

nomenclature for ‘object types’ as set out in 5.2.7 Object nomenclature – Type

nomenclature for ‘object occurrences’ (referred to as Components in COBie) as set out in 5.2.8 Object nomenclature – Occurrence

nomenclature for ‘systems’ as set out in 5.2.9 System nomenclature

models which are required to provide ‘properties’ (referred to as Attributes in COBie) in line with the exchange information requirements. All properties shall be provided in the correct ‘property sets’ in line with the exchange information requirements

where COBie is to be delivered all fields which correspond to a Picklist shall conform to the requirements as set out in 5.2.10 COBie picklists

### 4.1.3 Acceptable alternative IFC-SPF to COBie workflows

The Detailed Exchange Information Requirements include supporting information setting out a complete list of required IFC properties and property sets. The following specific points are noted:

Attributes related to System data: whilst the IFC2x3 schema and COBie Responsibility Matrix v17 use IfcSystem to deliver System data it is recognised that some authoring tools do not yet fully support IfcSystem data for all objects or the creation of this data can be difficult and time consuming. Therefore, an alternative acceptable workflow is to use properties associated to objects. The following properties shall be used within IFC-SPF: ‘SystemCategory’, ‘SystemDescription’ and ‘SystemName’ and provided in a Property Set called ‘Additional_Pset_SystemCommon’. It should be noted that with this workflow it would not be possible to populate the ExtIdentifier field required by COBie with a GlobalId (GUID) from an IfcSystem

Attributes related to Electric Distribution Points: where Electric Distribution Points are included in COBie it is necessary with an IFC2x3 TC1 workflow to create an alternative workflow. This is because types are not supported in the IFC2x3 TC1 schema. The alternative workflow is to include the following properties at occurrence level within IFC-SPF: ‘IfcName’ and ‘IfcDescription’ provided in a Property Set called ‘Additional_Pset_ElectricDistributionPointCommon’

## 4.2 COBie (Construction Operations Building information exchange)

COBie (Construction Operations Building information exchange) is an industry standard set out in the UK by BS EN ISO 19650-4:2022, that allows the transfer of information from the design and construction phases to the operational phase.

The specific COBie requirements, required information delivery milestones and maintainable assets are set out separately in the Detailed Exchange Information Requirements.

The following shall be adhered when producing COBie:

COBie shall be delivered as a single model in “an XML schema for Microsoft Excel spreadsheet 2003”

all COBie sheets, columns and header rows shall be retained (nothing to be deleted or re-ordered)

cell colouration, formatting and validation shall be retained

the instruction sheet shall be included with: Title, Version, Release, Status and Region

additional Picklists shall occur to the right of the standard Picklists included in the COBie template

a COBie output shall be produced for each (separate) asset

all sheets, columns and header rows shall be present in the deliverable and named and ordered in the same way as the standard. A blank row shall not occur before a row containing data or a header

data types shall be consistent with the COBie v2.4 template

dates shall be presented in accordance with BS ISO 8601-1:2019+A1:2022 / BS ISO 8601-2:2019. The time component is optional

every required reference to other sheets is valid (this includes references to Picklists)

enumerations specified in the Attributes and Picklists shall be adhered to

the uniqueness of information shall be ensured. Names shall be unique within their sheet, except that the System, Zone and Attribute names shall be unique in conjunction with other columns

on the “Attribute” sheet, every Attribute Name (column A), taken with Sheet-Name (column E) and Row-Name (column F) shall be unique

on the “System” sheet, every System Name (column A) taken with Component-Names (column E) shall be unique

on the “Zone” sheet, every Zone Name (column A) taken with Space-Names (column E) shall be unique

naming shall be in accordance with BS 8541-1:2012 clause 4.3.1

names shall use the characters A-Z, a-z and 0-9 with spaces and full stops

contacts shall be named by use of their valid email address, including “@”

names shall not contain commas or double spaces, nor unusual characters (i.e., • , . ! “ £ $ % ^ & * ( ) { }[ ] + = < > ? | \ / @ ’ ~ #¬ ` ‘). The hyphen/minus character is allowable

classifications shall use a space, colon and space “ : ” to separate code from description and not use commas

units shall be in accordance with 2.2.7 Units and measurement which is compliant with the requirements of BS EN ISO 19650-2 NA.2.5 Units

Length, Area and Volume and Currency values shall be consistent with the units selected on the Facility sheet

COBie deliverables shall have continuity with earlier deliverables and preferably be developed cumulatively to allow comparison and checking

unique asset names shall be maintained from earlier deliverables

the External System identifiers such as Globally Unique Identifiers (GUIDs) shall be maintained (it is noted that some authoring applications do not support or make optional the maintenance of the GUID during design development)

Constant Attributes (excluding identification, quantities and location details) shall be assigned to:

  - the Type or System, not the Component, and

  - the Floor (region) or Zone, not the Space (location)

the relevant groupings used to manage the Facility shall be provided. Every identifiable Space (location) shall be assigned to at least one Zone and to a Floor (region). Every manageable Component shall be assigned to at least one System and to a Type

Category entries shall be provided

an operational Job and an operational Spare shall be completed with a Type reference

operational Jobs shall be annotated with operational Resources

the following shall not be documented as Attributes:

  - zero, unset or undefined Values

  - graphical and stylistic information

  - parametric behaviour, and

  - information found elsewhere in COBie

models delivered using IFC-SPF shall conform to the 'Spreadsheet Schema' tab of the COBie Responsibility Matrix v17

documents listed in the information deliverables are referenced on the Document sheet. As a minimum all Documents shall be referenced to the Facility, although information related to specific product types (e.g., Warranties) shall be associated to the specific product

Any additional Attributes shall be taken from PAS/ISO 16739:2005 (IFC2x3 TC1) or ISO 16739-1:2024 (IFC4.3 ADD2).

For the Space Category field in COBie this shall be populated with the ‘Code’ and ‘Space/Place name’ in the Data Library separated by a space, colon and space in lieu of Uniclass SL Spaces/ locations information. The Uniclass SL Spaces/ locations reference shall be provided, but in a field entitled ‘UniclassClassification’.

## 4.3 COBie Quality Control (QC) Report

A COBie Quality Control (QC) Report shall be provided for each COBie file delivered at each information exchange. The COBie Quality Control (QC) Report shall demonstrate compliance of the COBie file with the COBie schema based on the rules outlined within the NBIMS COBie "Quality control test rule definition". The report shall be uploaded to the project’s common data environment.

The QC reporter can report on items not required to be delivered to DfE.

## 4.4 Native drawings

All Native drawing (DWG/DXF) files shall have layers that conform to the requirements set out in 4.6 Layer requirements.

## 4.5 Classification and categorisation

Classification requirements are identified in this section.

### 4.5.1 Asset classification

Classification allows data to be organised consistently in a structured manner. There are a number of classification systems (e.g., Omniclass, Uniclass etc) available and also published lists (e.g., NRM, SFG20 etc).

For this project the primary classification to be used for information shall be Uniclass. Uniclass is the UK implementation of BS ISO 12006-2.

More about Uniclass can be found here:

https://www.thenbs.com/knowledge/what-is-uniclass

Current searchable Uniclass tables are also available here:

https://uniclass.thenbs.com/

The following classification shall be used for IFC-SPF and COBie delivery:

| IFC | COBie | Classification Name | Source | Version | Date |
| --- | --- | --- | --- | --- | --- |
| n/a | Contact | n/a | Uniclass Ro Roles | vX.X | Month 202X |
| IfcBuilding | Building | Uniclass Classification | Uniclass En Entities | vX.X | Month 202X |
| IfcBuildingStorey | Floor | Floor Classification | 5.2.4 Category | n/a | n/a |
| IfcSpace | Space | Uniclass Classification | Uniclass SL Spaces/ locations | vX.X | Month 202X |
| IfcSpace | Space | DfE Space Classification | Spaces / Places Data Library | CXX | Month 202X |
| IfcZone | Zone | Zone Classification | 5.2.6 Category | n/a | n/a |
| IfcProductType | Type | Uniclass Classification | Uniclass Pr Products or EF Elements/functions (non-COBie entities only) | vX.X | Month 202X |
| IfcSystem | System | Uniclass Classification | Uniclass Ss Systems | vX.X | Month 202X |
| n/a | Document | Uniclass Classification | Uniclass PM Project management | vX.X | Month 202X |
| IfcPresentationLayerAssignment | n/a | Uniclass Classification | Uniclass Zz CAD (plus above as required) | vX.X | Month 202X |

All products for COBie shall use the ‘Uniclass Pr Products’ table but those outside of the scope of COBie may use a combination of ‘Uniclass EF Elements/ functions’ and ‘Uniclass Pr Products’ tables.

Classification shall be exported to IFC as a classification using the IFC classification name listed above.

### 4.5.2 Costing classification

The following classification tables shall be used for costing:

| Name | Description |
| --- | --- |
| NRM1 | RICS new rules of measurement: Order of cost estimating and cost planning for capital building works |
| NRM2 | RICS new rules of measurement: Detailed measurement for building works |
| NRM3 | RICS new rules of measurement: Order of cost estimating and cost planning for building maintenance works |

## 4.6 Layer requirements

Layering for all DWG and IFC-SPF outputs shall conform to BS EN ISO 13567-2.

Not all authoring tools utilise layers in their model creation, but all DWG and IFC-SPF outputs shall align to the requirements set out in this section.

### 4.6.1 Layer format

The following format shall be used:

Agent-Element-Presentation-Description

### 4.6.2 Agent

Agent code shall be taken from Discipline codes documented in 5.1.3 Originator codes.

For single character codes the agent shall be followed by a hyphen e.g., A-

For two character codes the agent shall be provided without a hyphen.

### 4.6.3 Element

Element shall use Uniclass classification (using the appropriate table as required). Codes shall be restricted to 6 characters and underscores removed, in line with the requirements of BS EN ISO 13567-2.

For example ‘Ss_25_10_20’ would be provided as ‘Ss2510’.

### 4.6.4 Presentation

Presentation code provided shall be -- (2 hyphens).

### 4.6.5 Description

Description shall be a valid Uniclass description. Descriptions from the available tables shall be changed to PascalCase accordingly.

Current Uniclass tables can be found here: https://uniclass.thenbs.com/

### 4.6.6 Example layers

Example 1 - an architectural layer for curtain walling would be:

A-Ss2510--CurtainWallingSystems

Example 2 - a structural layer for a column would be: S-Ss2030—Columns

# 5 Nomenclature

This section sets out standard nomenclature for the project.

This includes file naming, information containers, descriptions, and standardised values.

Nomenclature shall not contain any of the following characters or double spaces:

• , . ! “ £ $ % ^ & * ( ) { }[ ] + = < > ? | \ / @ ’ ~ #¬ ` ‘ :

The hyphen/minus character shall only be allowed when used as a separator for the information container fields.

## 5.1 File naming, revisions and status

The file naming (referred to as information containers in ISO 19650) is fully aligned with the UK National Annex of BS EN ISO 19650-2 (incorporating corrigendum February 2021) and aims to succinctly extract the required guidance and best practice for standardising information naming at a project level, for all participants producing information.

### 5.1.1 File naming format

All shared and published project information shall comply with the following file container naming standard, as set out in BS EN ISO 19650-2.

Names shall be created by joining together codes in the specified mandatory fields indicated below separated by a “-“ hyphen character, which is therefore not allowed in any code:

Project-Originator-Functional Breakdown-Spatial Breakdown-Form-Discipline-Number

Note 1: The term ‘information container’ is used to describe the file name made up of the fields indicated above.

Note 2: The file ‘description’ is optional text that if required shall follow the number code preceded by a “-” hyphen character. Typically, the ‘description’ will be inputted as metadata managed in the project’s common data environment.

Note 3: Status codes and revision codes shall not typically form part of the information container name, as these will be inputted as metadata managed in the project’s common data environment. The only exception for status and revision code to be appended to the information container name, is in accordance with 5.1.10 File naming examples, specifically ‘Example 3’.

### 5.1.2 Project code

Project-Originator-Functional Breakdown-Spatial Breakdown-Form-Discipline-Number

A single common project code shall be defined at the initiation of the project, which shall be independent from any individual organisation’s internal project number. This shall be the Scheme/Project contract code.

The project code aligns to the requirements of BS EN ISO 19650-2 NA.3.2 Project.

Refer to 5.2.1 Project nomenclature for Project Code.

### 5.1.3 Originator codes

Project-Originator-Functional Breakdown-Spatial Breakdown-Form-Discipline-Number

A unique identifier shall be defined for each organisation on joining the project, to identify the organisation responsible for producing the information within the information container.

Each organisation involved with the project shall be assigned a three character ‘Originator’ code to identify the source of the information.

Where more than one Originator has provided information for the same role, separate rows shall be added to the table below to differentiate each Originator. This is particularly important where the same roles exist for multiple Lead Appointed Parties (e.g., Architects appointed by both Technical Advisors and Contractors).

Originator codes specified in line with BS EN ISO 19650-2 NA.3.3 Originator as shown below:

| Role | Uniclass Ro Role | Code | Discipline | Organisation |
| --- | --- | --- | --- | --- |
| Access consultant | Ro_50_10_01 | TBC | O | TBC |
| Acoustic engineer | Ro_50_20_02 | TBC | J [ii] | TBC |
| Arboriculturalist | Ro_50_30_04 | TBC | O | TBC |
| Archaeologist | Ro_70_30_04 | TBC | O | TBC |
| Architect | Ro_50_10_03 | TBC | A | TBC |
| Building control officer | Ro_30_30_09 | TBC | T | TBC |
| Building surveyor | Ro_70_10_11 | TBC | B | TBC |
| Catering consultant | Ro_50_10_11 | TBC | O | TBC |
| Civil engineer | Ro_50_20_11 | TBC | C | TBC |
| Clerk of works | Ro_30_10_13 | TBC | O | TBC |
| Client | Ro_10_20_14 | DFE | X | Department for Education |
| Contractor | Ro_30_10_20 | TBC | X | TBC |
| Cost manager | Ro_10_40_22 | TBC | Q | TBC |
| Education consultant | Ro_10_30_27 | TBC | O | TBC |
| Ecologist | Ro_50_30_25 | TBC | O | TBC |
| Electrical services engineer | Ro_50_20_30 | TBC | E [i] | TBC |
| Environmental consultant | Ro_70_30_28 | TBC | O | TBC |
| Fittings, furniture and equipment (FF&E) consultant | Ro_50_10_30 | TBC | O | TBC |
| Fire engineer | Ro_50_20_33 | TBC | K [ii] | TBC |
| Geotechnical surveyor | Ro_70_10_33 | TBC | O | TBC |
| Heritage surveyor | Ro_70_10_36 | TBC | O | TBC |
| Highways engineer | Ro_50_20_41 | TBC | H | TBC |
| Hydrologist | Ro_70_30_39 | TBC | W | TBC |
| Information manager (DfE) | Ro_30_10_42 | Role performed by Technical advisor Email: email@example.com | Role performed by Technical advisor Email: email@example.com | Role performed by Technical advisor Email: email@example.com |
| Information manager (Contractor) | Ro_30_10_42 | Role performed by Contractor Email: email@example.com | Role performed by Contractor Email: email@example.com | Role performed by Contractor Email: email@example.com |
| Interior designer | Ro_50_10_43 | TBC | I | TBC |
| Land surveyor | Ro_70_10_46 | TBC | Y | TBC |
| Landscape architect | Ro_50_30_47 | TBC | L | TBC |
| Lighting designer | Ro_50_10_50 | TBC | O | TBC |
| Mechanical services engineer | Ro_50_20_54 | TBC | M [i] | TBC |
| Party wall surveyor | Ro_30_30_60 | TBC | O | TBC |
| Planning consultant | Ro_70_10_64 | TBC | T | TBC |
| Principal designer | Ro_30_30_68 | TBC | O | TBC |
| Project manager | Ro_30_10_67 | DFE | R | Department for Education |
| Public health engineer | Ro_50_20_68 | TBC | P [i] | TBC |
| Quantity surveyor | Ro_70_10_75 | TBC | Q | TBC |
| Security consultant | Ro_10_40_76 | TBC | O | TBC |
| Signage designer | Ro_50_10_80 | TBC | O | TBC |
| Site investigation consultant | Ro_70_10_80 | TBC | O | TBC |
| Soft landings champion | Ro_10_30_78 | Role performed by DfE’s Project manager | Role performed by DfE’s Project manager | Role performed by DfE’s Project manager |
| Structural engineer | Ro_50_20_83 | TBC | S | TBC |
| Subcontractor | Ro_30_10_85 | TBC | X | TBC |
| Sustainability consultant | Ro_70_30_85 | TBC | O | TBC |
| Technical advisor | Ro_10_20_88 | TBC | X | TBC |
| Traffic engineer | Ro_50_20_90 | TBC | O | TBC |
| Utilities surveyor | Ro_70_10_93 | TBC | O | TBC |
| Utilities surveyor | Ro_70_10_93 | TBC | Y [iii] | TBC |

[i] Where information is issued for ‘multiple disciplines’ then ‘Z’ shall be used as the Discipline code.

[ii] Codes allocated by DfE in addition to standard ISO 19650-2 National Annex codes.

[iii] The use of ‘Y’ as the discipline code is applicable to topographical surveys of utilities.

### 5.1.4 Functional breakdown codes

Project-Originator-Functional Breakdown-Spatial Breakdown-Form-Discipline-Number

A unique identifier shall be defined for the functional aspects of the information container breakdown structure. This can be based on physical subdivision (such as major design elements or systems) or notional subdivision (such as security classification).

Functional Breakdown identifiers in a school/college project shall include codes for existing and new buildings or blocks that form part of the project.

Each Functional Breakdown shall be given a code comprising two characters.

Functional Breakdown codes are specified in line with BS EN ISO 19650-2 NA.3.4 Functional Breakdown as shown below:

| Code | Description | Build Type | Condition Data Collection (CDC) code |
| --- | --- | --- | --- |
| ZZ | multiple subdivisions apply to this information container | n/a | n/a |
| XX | no sub-division is applicable to this information container | n/a | n/a |
| 00 | Site | n/a | n/a |
| 01 | Building 01: Block/Building Description/Name | New Build/Existing Building | CDC code if existing and retained |
| ?? | additional codes as proposed by the Contractor | - | - |

Functional Breakdown shall be determined by the project team at the outset and managed at the highest level of the project management team therein. It is recommended that the Functional Breakdown code used relates to the 'Blocks' or 'Buildings' set out in 5.2.3 Building(s) nomenclature in a sequential numerical order. The sequence shall prioritise new buildings over refurbished buildings and those targeted for demolition.

### 5.1.5 Spatial breakdown codes

Project-Originator-Functional Breakdown-Spatial Breakdown-Form-Discipline-Number

Each level in the project shall be assigned a two-character code to identify the Spatial Breakdown, and this shall be identified where applicable to each file container name.

Spatial Breakdown codes are specified in line with BS EN ISO 19650-2 NA.3.5 Spatial Breakdown.

Refer to 5.2.4 Building storey (Floor) nomenclature for Spatial Breakdown codes.

### 5.1.6 Form codes

Project-Originator-Functional Breakdown-Spatial Breakdown-Form-Discipline-Number

The ‘form’ code is an alphanumerical code that indicates the form of information of the information deliverable to be provided.

Type codes have been aligned with BS EN ISO 19650-2 NA.3.6 Form as shown below:

| Code | Form | Description |
| --- | --- | --- |
| D | drawing | Information in the form of a graphical depiction of shape, size, etc., of a physical part or assembly, usually to scale |
| G | diagram | Information in the form of a graphical/symbolic depiction showing the functions of the objects composing a system and their interrelationships using graphical elements and symbols, or the behaviour of variables using graphs |
| I | image | Information in the form of a static image or picture and not defining any relationships between objects |
| L | list | Information in the form of columns and rows, such as tables, spreadsheets and datasets |
| M | model | Two‐ or three‐dimensional physical or digital description of the ideal shape of object(s) and/or space(s) |
| T | textual | Information in the form of characters and paragraphs - for example in written instructions and descriptions |
| V | video/audio | Information in the form of moving images, animation or sound |

### 5.1.7 Discipline codes

Project-Originator-Functional Breakdown-Spatial Breakdown-Form-Discipline-Number

Each organisation shall be allocated to one or more roles within the project. Codes for the Discipline field are to be one character in length. Discipline codes are specified in line with BS EN ISO 19650-2 NA.3.7 Discipline as shown below:

| Code | Discipline |
| --- | --- |
| A | architecture |
| B | building surveyor |
| C | civil engineering |
| D | demolition/dismantling |
| E | electrical engineering |
| F | facilities/asset management |
| G | ground engineering |
| H | highways and transport engineering |
| I | interior architecture * |
| J | acoustic engineering * |
| K | fire engineering * |
| L | landscape architecture |
| M | mechanical engineering |
| N | spare |
| O | other discipline |
| P | public health engineering |
| Q | quantity surveying / cost consultancy |
| R | project management |
| S | structural engineering |
| T | town and country planning and building control |
| U | spare |
| V | spare |
| W | water engineering |
| X | non-discipline specific or not applicable |
| Y | topographical surveying |
| Z | multiple disciplines |

*Spare codes allocated by the DfE for consistency across projects.

### 5.1.8 Number codes

Sequential/grouped number to make the ID unique when all other fields are taken into account.

Project-Originator-Functional Breakdown-Spatial Breakdown-Form-Discipline-Number

In accordance with the National Annex the number code is fixed within this Project’s Information Standard and shall be exactly four integer numeric digits, with no special characters such as underscores or hyphens. A sequential number shall be assigned to each information container when it is one of a series, not distinguished by any other of the fields.

### 5.1.9 Status and revision codes

The following status and revision codes shall be used for this project:

| Code | Description | Revision |
| --- | --- | --- |
| Work in progress (WIP) | - | - |
| S0 | Information container being developed within a task team | P01.01 to Pnn.nn |
| Shared (non-contractual) | - | - |
| S1 | Information containers that are suitable for geometrical and/or non‐geometrical coordination within a delivery team | P01 to Pnn |
| S2 | Information containers that are suitable for information/ reference by other task teams within a delivery team | P01 to Pnn |
| S3 | Information containers that are suitable for review and comment within a delivery team | P01 to Pnn |
| S4 | Information containers that are suitable for review and authorisation by the Lead Appointed Party (Contractor) | P01 to Pnn |
| S5 | Information containers suitable for review and acceptance by the Department for Education (DfE) | P01 to Pnn |
| Published (contractual) | - | - |
| A | Accepted for all RIBA Stages as complete by DfE | C01 to Cnn |
| A0 | Accepted in RIBA Stage 0 as complete by DfE | C01 to Cnn |
| B0 | Accepted with comments in RIBA Stage 0 as complete by DfE | C01 to Cnn |
| A1 | Accepted in RIBA Stage 1 as complete by DfE | C01 to Cnn |
| B1 | Accepted with comments in RIBA Stage 1 as complete by DfE | C01 to Cnn |
| A2 | Authorised in RIBA Stage 2 as complete by the Contractor OR Accepted in RIBA Stage 2 as complete by DfE | C01 to Cnn |
| B2 | Authorised with comments in RIBA Stage 2 as complete by the Contractor OR Accepted with comments in RIBA Stage 2 as complete by DfE | C01 to Cnn |
| A3 | Authorised in RIBA Stage 3 as complete by the Contractor OR Accepted in RIBA Stage 3 as complete by DfE | C01 to Cnn |
| B3 | Authorised with comments in RIBA Stage 3 as complete by the Contractor OR Accepted with comments in RIBA Stage 3 as complete by DfE | C01 to Cnn |
| A4 | Authorised in RIBA Stage 4 as complete by the Contractor OR Accepted in RIBA Stage 4 as complete by DfE | C01 to Cnn |
| B4 | Authorised with comments in RIBA Stage 4 as complete by the Contractor OR Accepted with comments in RIBA Stage 4 as complete by DfE | C01 to Cnn |
| A5 | Authorised in RIBA Stage 5 as complete by the Contractor OR Accepted in RIBA Stage 5 as complete by DfE | C01 to Cnn |
| B5 | Authorised with comments in RIBA Stage 5 as complete by the Contractor OR Accepted with comments in RIBA Stage 5 as complete by DfE | C01 to Cnn |
| A6 | Authorised as in RIBA Stage 6 as complete by the Contractor OR Accepted in RIBA Stage 6 as complete by DfE | C01 to Cnn |

If a deliverable is assigned ‘Bn’ status, the Contractor (Lead Appointed Party) may proceed in accordance with that deliverable, provided that DfE’s (Appointing Party) comments are incorporated into it and an amended copy of it is promptly submitted to the DfE. This takes precedence over any different interpretation of the 'Bn' status code in the ISO 19650 National Annex.

### 5.1.10 File naming examples

Taken from the codes defined in the previous sections, the example file names below reflect a door schedule produced by the architecture discipline and applicable to multiple functional and spatial breakdowns.

Example 1 (default):

ABCDE-XYZ-ZZ-ZZ-L-A-0001

Example 1 is the default compliant file name method where the file ‘description’, ‘status code’ and ‘revision code’ are entered as metadata and managed in the project’s common data environment.

Example 2 (including optional ‘description’ field)

ABCDE-XYZ-ZZ-ZZ-L-A-0001-Door Schedule

Example 2 includes the optional file ‘description’ in the native file container name. The file description shall be consistent across the project’s common data environment, Master Information Delivery Plan, Title Blocks and where used in COBie Documents for Description and File information. Each word shall be capitalised e.g., GA Floor Plan. Spaces or underscores can be used between words.

Example 3 (for files outside the project’s common data environment)

ABCDE-XYZ-ZZ-ZZ-SH-L-0001-Door Schedule-S3-P01

Example 3 includes the ‘description’, ‘status code’ and ‘revision code’ in the native file container name. Files shall only include status codes and revision codes when being stored separately outside of the project’s common data environment. Using status and revision codes in native file names would mean file history is not maintained in the project’s common data environment and multiple versions of the same file would exist. File descriptions shall be separated from the number code using a hyphen only. Spaces or underscores can be used between words in the file description, but hyphens and special characters shall be avoided.

### 5.1.11 Information container structures

The following information containers have a defined structure to be provided:

| Description | Information container structure requirement |
| --- | --- |
| Health and Safety File | Refer to Appendix B |
| Building Log Book | Refer to Appendix C |
| Building User Guide | Refer to Appendix D |

## 5.2 Standardised values

### 5.2.1 Project nomenclature

This section sets out key information about the project:

| Field | Value |
| --- | --- |
| Project code | ABC1234 |
| Project name | Name of Project (e.g., Catherine Primary School) |
| Project description | Indicative build type, Form of entry, Education Type (e.g., New build one form entry primary school) |

Where shared resources are produced for the DfE Construction Framework 2025 these will contain ‘FRM2025’ or for the DfE Technical Advisory Services 2025 these will be ‘TAS2025’ as the project code rather than the project specific code. Information shared on projects shall always use the specific project code set out in this resource so any shared resources shall be renamed accordingly.

References to ‘Scheme’ in contractual documentation, resources and data are deemed to equate to ‘Project’.

### 5.2.2 Site nomenclature

This section sets out key information about the site:

| Field | Value |
| --- | --- |
| Site name | Short Site Location (e.g., Road Name and Town or Site name and Town) |
| Site description | Total Site Area and Long Site Location including Bounding Features (e.g., 13700m2 site located to North East of Leicester and sits delineated on three sides by Ulverscroft Road Catherine Street and Martin Street) |

### 5.2.3 Building(s) nomenclature

This section sets out key information about the building(s):

| Field | Value |
| --- | --- |
| Building name | Name of the School/College and Building number (e.g., Catherine Primary School Building 01 or St Martins Secondary School Building 03) |
| Building description | Education Type, building number and building description/name (e.g., Primary school building 01 for teaching or Primary school building 01 newton block) |
| Building Category (Uniclass En Entities) | En_XX_XX_XX: Description |
| Unique Property Reference Number (UPRN) | TBC |

The table shall be duplicated if multiple separate buildings are being delivered as part of the same project.

If the project does not yet have a UPRN, the Project's Information Standard shall use a placeholder value of ‘n/a’ and be updated as and when available.

### 5.2.4 Building storey (Floor) nomenclature

This section sets out key information about the building storeys (Floors). The codes below are preferred and shall be used unless otherwise agreed with the DfE’s Technical Advisor:

| Name | Code | Description | Category | Elevation (mm) | Height (mm) |
| --- | --- | --- | --- | --- | --- |
| n/a | XX | no spatial sub-division is applicable | n/a | n/a | n/a |
| n/a | ZZ | multiple spatial sub-divisions are applicable | n/a | n/a | n/a |
| Level B2 | B2 | Basement level 2 | Floor | TBC | TBC |
| Level B1 | B1 | Basement level 1 | Floor | TBC | TBC |
| Level EX | EX | Site level | Site | TBC | TBC |
| Level 00 | 00 | Base level of building | Floor | TBC | TBC |
| Level M0 | M0 | Mezzanine above base level | Floor | TBC | TBC |
| Level 01 | 01 | First floor | Floor | TBC | TBC |
| Level M1 | M1 | Mezzanine above first floor | Floor | TBC | TBC |
| Level 02 | 02 | Second floor | Floor | TBC | TBC |
| Level 03 | 03 | Third floor | Floor | TBC | TBC |
| Level 04 | 04 | Fourth floor | Floor | TBC | TBC |
| Level RF | RF | Main roof | Roof | TBC | TBC |
| Level R2 | R2 | Additional roof above main roof | Roof | TBC | TBC |

This table shall also be used to set out the Spatial Breakdown for the project.

Elevation shall be relative to above sea level to comply with COBie requirements (discrepancy noted between NBIMS v3 4.2 COBie relative to Facilities Datum and IFC2x3 TC1 relative to Internal Datum).

Height shall be the distance between a building storey finished floor level (FFL) to the underside of the structure above to comply with COBie requirements. Where software limitations do not accurately report this, an additional property of ‘NetHeight’ can be added to a custom property set under ‘Additional_Pset_BuildingStoreyCommon' for accurate reporting.

Definitions of Elevation and Height shall be provided by the selected Contractor within their (pre-appointment) BIM Execution Plan Appendix (refer to EIR Section D3).

### 5.2.5 Space nomenclature

Space Name

Space Names shall be provided by the Architect for all Spaces within the building and by the Landscape Architect for all Spaces outside the building, including all Spaces that contain maintainable assets.

Spaces shall be numbered clockwise from the main entrance. Task Teams may include additional data within the native model to allow for unique room identification until layouts are fixed.

The space name shall use the following convention where the fields are separated by a hyphen:

<Floor code>–<sequential number>

Field 1 – Floor code Floor codes shall be taken from the nomenclature defined in 5.2.4 Building storey (Floor) nomenclature.

Field 2 – Sequential Number A unique number (once per level) identifying the room. Use 3-digits for consistency.

Example: Space number 35 on Level 02 would be 02-035

Space nomenclature shown on drawings and schedules shall be provided in the exported IFC-SPF and in the COBie output(s).

Space Category

The Space Category for Spaces in COBie shall use the ‘Code’ combined with the ‘Space name’ in the Data Library separated by a space, colon and space (e.g., ‘ACT01 : Dance studios’).

The Space Category for Places in COBie shall use the ‘Code’ combined with the ‘Place name’ in the Data Library separated by a space, colon and space (e.g., HIS12 : Outdoor training spaces).

Room Tag

The Room Tag field represents the final room signage to be provided for each Space. This data is in addition to the Space Names and shall be provided by the School/College to the Contractor during RIBA Stage 5: Manufacturing and Construction.

Uniclass Classification

The required Uniclass Classification is set out against each ‘Code’ in the Data Library for Spaces and Places respectively.

### 5.2.6 Zone nomenclature

This section sets out the zone nomenclature for the project:

| Name | Description | Category | HEX | RGB |
| --- | --- | --- | --- | --- |
| Basic teaching | Classrooms, playrooms, ICT, light practical spaces and heavy practical spaces | Net | #FFCC99 | 255, 204,153 |
| Halls and dining | Halls, activity studios, sports halls, dining and social areas | Net | #92D050 | 146, 208, 80 |
| Learning resources | Libraries and study areas, arts & DT learning resources and SEN and support spaces | Net | #FEFEA5 | 254, 254, 165 |
| Non-net | School kitchen spaces, changing rooms, toilets and hygiene rooms, plant areas and circulation areas | Non-net | #BFBFBF | 191, 191, 191 |
| Residential | Residential accommodation | Net | #FFE699 | 255, 230, 153 |
| Staff and administration | Administration and entrances, administration offices, offices, staff work rooms and other staff spaces | Net | #9BC2E6 | 155, 194, 230 |
| Storage | Storage spaces for teaching, personal, admin, and maintenance items | Net | #CC99FF | 204, 153, 255 |
| Hard informal and social area | Hard informal and social areas | Net Site | #E6B8B7 | 230, 184, 183 |
| Hard outdoor PE | Hard outdoor physical education areas | Net Site | #CCC0DA | 204, 192, 218 |
| Habitat | Habitat supervised areas | Net Site | #B7DEE8 | 183, 222, 232 |
| Soft informal and social area | Soft informal and social areas | Net Site | #A9D08E | 169, 208, 142 |
| Soft outdoor PE | Soft outdoor physical education areas | Net Site | #E2EFDA | 226, 239, 218 |
| Non-net site area | Non-net site areas | Non-net Site | #D9D9D9 | 217, 217, 217 |
| Entrance landscape | - | Character Area | #F7CFBB | 247, 207, 187 |
| Courtyard garden | - | Character Area | #FAEABC | 250, 234, 188 |
| Parkland and playing fields | - | Character Area | #DAE3C3 | 218, 227, 195 |
| Playscape | - | Character Area | #CBE7E6 | 203, 231, 230 |

The HEX and RGB values in this table are provided to allow consistency of colour display across projects where information is displayed as data in schedules or as diagrams only.

In IFC-SPF Zones have no specific physical geometry but the relationship between Space and Zone can be used to visualise this data if required.

Each space to zone relationship must be entered as a separate row in the Zone worksheet with identical Zone.Name values for spaces in the same zone. Concatenated lists in the Zone.SpaceNames field are not permitted (deprecated in COBie 2.4).

### 5.2.7 Object nomenclature – Type

Object type nomenclature shall follow the following convention:

| Field 1 | Field 2 | Field 3 |
| --- | --- | --- |
| Entity – See list provided in 5.2.8 | Enumeration (Predefined Type) – See list provided in 5.2.8 | TypeXX |

Object type nomenclature shall adhere to the following:

all Xs are to be replaced by sequential numbers

each field shall be separated by an underscore

where an Enumeration (Predefined Type) has been listed under Section 5.2.8 as ‘n/a’, this field shall be omitted

Enumeration (Predefined Type) shall be provided in PascalCase rather than in Capitals i.e., an ELECTRICACTUATOR shall be expressed as ‘ElectricActuator’

field 2 shall match the Predefined Type it is relative to e.g., A Predefined Type of JOIST for a Beam shall read ‘Joist’. However, for USERDEFINED entities the user is free to create their own logical description provided it is shown in PascalCase

  - USERDEFINED types shall be communicated in the Contractor’s (pre-appointment) BIM execution plan during tender response phase. These shall be incorporated by the Technical Advisor into the Detailed Exchange Information Requirements ‘B_IFC_EnumerationDefinitions’ worksheet

  - the term ‘USERDEFINED’ shall not be used within field 2, only the user defined value(s)

  - the USERDEFINED attribute assigned against IfcElementType shall be provided in PascalCase rather than in Capitals i.e., a rectangular column shall be expressed as ‘Column_Rectangular_Type01’

  - IfcElementType shall be provided in Capitals i.e., RECTANGULAR

field 3 can be adjusted to suit but is generally preferred if it includes the word ‘Type’ followed by numbers, letters or other sensible designation. Unusual characters (see earlier) shall be avoided i.e., Door_TypeE01

where agreed across a project team an additional field can be used at the start of the sequence to identify the Discipline. Any Discipline codes shall align with those documented in this Project’s Information Standard i.e., A_Door_Type01

where ‘Building Element Proxy’ entities exist, alternative descriptions may be used for Field 1 i.e., Other_Ladder_Type01

whilst entities such as Door, Furniture and Window do not have Predefined Types in IFC2x3 it is acceptable to use field 2 for these entities for further description i.e., Furniture_Desk_Type01 rather than simply Furniture_Type01

Examples:

Actuator_ElectricActuator_Type01, Actuator_ElectricActuator_Type02, Actuator_ElectricActuator_Type03 etc

Beam_Joist_Type01, Beam_Joist_Type02, Beam_Joist_Type03 etc

Door_Type01, Door_Type02, Door_Type03 etc

This nomenclature requirement applies to all model entities across all models.

### 5.2.8 Object nomenclature – Occurrence

This section sets out the object occurrence nomenclature for the project.

The format for the Name field for object occurrences is provided here as a best practice proposal. The exact Name format may be varied by the Contractor and delivery team provided the approach is documented against the IFC Entities and Predefined Types listed.

Note that occurrence nomenclature is only required against entities identified for planned preventative maintenance (PPM) (i.e., for inclusion in the COBie output(s)) – refer to the Detailed Exchange Information Requirements. However, where items outside of this scope are required for other purposes (e.g., on drawings or for scheduling) the table below shall be updated accordingly.

Any changes required by the Contractor and their delivery team shall be communicated through the (pre-appointment) BIM execution plan during the tender response phase. Agreed changes shall be incorporated by the Technical Advisor into this resource at Appointment stage.

To ensure consistency, the Name format for data outputs shall match all drawings and schedules.

The Name format may contain additional metadata to suit the Project, for example all formats can include the addition of a ‘Discipline’ code (i.e., in the format ‘?-XXX-XXXXX’ where ‘?’ is the Discipline from the codes set out in 5.1.7 of this resource) to avoid conflicts between different disciplines who are modelling similar entities.

Additionally, it may be appropriate to include Floor (Building Storey) or Space reference in advance of the Name format set out.

Any Naming format for loose furniture entities shall exclude any Floor (Building Storey) or Space references as these may change during the lifecycle of the asset.

| Entity | Enumeration (Predefined Type) | Name Format |
| --- | --- | --- |
| Actuator | ELECTRICACTUATOR | ATR-XXXXX |
| Actuator | HANDOPERATEDACTUATOR | ATR-XXXXX |
| Actuator | HYDRAULICACTUATOR | ATR-XXXXX |
| Actuator | PNEUMATICACTUATOR | ATR-XXXXX |
| Actuator | THERMOSTATICACTUATOR | ATR-XXXXX |
| Actuator | USERDEFINED | ATR-XXXXX |
| Air Terminal | DIFFUSER | ASD-XXXXX (Supply) AED-XXXXX (Extract) |
| Air Terminal | EYEBALL | AIR-XXXXX |
| Air Terminal | GRILLE | AEG-XXXXX (Louvre) |
| Air Terminal | IRIS | AIR-XXXXX |
| Air Terminal | LINEARDIFFUSER | ASD-XXXXX (Supply) |
| Air Terminal | LINEARGRILLE | AEG-XXXXX (Louvre) |
| Air Terminal | REGISTER | AIR-XXXXX |
| Air Terminal | USERDEFINED | ATG-XXXXX (Transfer Grille) |
| Air Terminal Box | CONSTANTFLOW | ATB-XXXXX |
| Air Terminal Box | USERDEFINED | PLB-XXXXX (Plenum Box) BC-XXXXX (VRF Branch Controller Box) |
| Air Terminal Box | VARIABLEFLOWPRESSUREDEPENDANT | ATB-XXXXX |
| Air Terminal Box | VARIABLEFLOWPRESSUREINDEPENDANT | ATB-XXXXX |
| Air To Air Heat Recovery | FIXEDPLATECOUNTERFLOWEXCHANGER | ATA-XXXXX |
| Air To Air Heat Recovery | FIXEDPLATECROSSFLOWEXCHANGER | ATA-XXXXX |
| Air To Air Heat Recovery | FIXEDPLATEPARALLELFLOWEXCHANGER | ATA-XXXXX |
| Air To Air Heat Recovery | HEATPIPE | ATA-XXXXX |
| Air To Air Heat Recovery | ROTARYWHEEL | ATA-XXXXX |
| Air To Air Heat Recovery | RUNAROUNDCOILLOOP | ATA-XXXXX |
| Air To Air Heat Recovery | THERMOSIPHONSEALEDTUBEHEATEXCHANGERS | ATA-XXXXX |
| Air To Air Heat Recovery | THERMOSIPHONCOILTYPEHEATEXCHANGERS | ATA-XXXXX |
| Air To Air Heat Recovery | TWINTOWERENTHALPYRECOVERYLOOPS | ATA-XXXXX |
| Air To Air Heat Recovery | USERDEFINED | ATA-XXXXX |
| Alarm | BELL | ALR-XXXXX |
| Alarm | BREAKGLASSBUTTON | ALR-XXXXX |
| Alarm | LIGHT | ALR-XXXXX |
| Alarm | MANUALPULLBOX | ALR-XXXXX |
| Alarm | SIREN | ALR-XXXXX |
| Alarm | USERDEFINED | ALR-XXXXX |
| Alarm | WHISTLE | ALR-XXXXX |
| Beam | BEAM | n/a |
| Beam | JOIST | n/a |
| Beam | LINTEL | n/a |
| Beam | T-BEAM | n/a |
| Beam | USERDEFINED | n/a |
| Boiler | STEAM | BLR-XXXXX |
| Boiler | USERDEFINED | BLR-XXXXX |
| Boiler | WATER | BLR-XXXXX |
| Building Element Proxy | USERDEFINED | DPO-XXXXX (Dosing Pot) WCD-XXXXX (Water Conditioner) WSO-XXXXX (Water Softener) OTH-XXXXX (Other) |
| Cable Carrier Fitting | BEND | n/a |
| Cable Carrier Fitting | CROSS | n/a |
| Cable Carrier Fitting | REDUCER | n/a |
| Cable Carrier Fitting | TEE | n/a |
| Cable Carrier Fitting | USERDEFINED | n/a |
| Cable Carrier Segment | CABLELADDERSEGMENT | n/a |
| Cable Carrier Segment | CABLETRAYSEGMENT | n/a |
| Cable Carrier Segment | CABLETRUNKINGSEGMENT | n/a |
| Cable Carrier Segment | CONDUITSEGMENT | n/a |
| Cable Carrier Segment | USERDEFINED | n/a |
| Cable Segment | CABLESEGMENT | n/a |
| Cable Segment | CONDUCTORSEGMENT | n/a |
| Cable Segment | USERDEFINED | n/a |
| Chiller | AIRCOOLED | CHL-XXXXX |
| Chiller | HEATRECOVERY | CHL-XXXXX |
| Chiller | USERDEFINED | CHL-XXXXX |
| Chiller | WATERCOOLED | CHL-XXXXX |
| Coil | DXCOOLINGCOIL | CCO-XXXXX |
| Coil | ELECTRICHEATINGCOIL | HCO-XXXXX |
| Coil | GASHEATINGCOIL | HCO-XXXXX |
| Coil | STEAMHEATINGCOIL | HCO-XXXXX |
| Coil | USERDEFINED | RAC-XXXXX (Run-Around) |
| Coil | WATERCOOLINGCOIL | CCO-XXXXX |
| Coil | WATERHEATINGCOIL | HCO-XXXXX |
| Column | COLUMN | n/a |
| Column | USERDEFINED | n/a |
| Compressor | BOOSTER | CMP-XXXXX |
| Compressor | DYNAMIC | CMP-XXXXX |
| Compressor | HERMETIC | CMP-XXXXX |
| Compressor | OPENTYPE | CMP-XXXXX |
| Compressor | RECIPROCATING | CMP-XXXXX |
| Compressor | ROLLINGPISTON | CMP-XXXXX |
| Compressor | ROTARY | CMP-XXXXX |
| Compressor | ROTARYVANE | CMP-XXXXX |
| Compressor | SCROLL | CMP-XXXXX |
| Compressor | SEMIHERMETIC | CMP-XXXXX |
| Compressor | SINGLESCREW | CMP-XXXXX |
| Compressor | SINGLESTAGE | CMP-XXXXX |
| Compressor | TROCHOIDAL | CMP-XXXXX |
| Compressor | TWINSCREW | CMP-XXXXX |
| Compressor | USERDEFINED | CMP-XXXXX |
| Compressor | WELDEDSHELLHERMETIC | CMP-XXXXX |
| Condenser | AIRCOOLED | CND-XXXXX |
| Condenser | EVAPORATIVECOOLED | CND-XXXXX |
| Condenser | USERDEFINED | CND-XXXXX |
| Condenser | WATERCOOLEDBRAZEDPLATE | CND-XXXXX |
| Condenser | WATERCOOLEDSHELLCOIL | CND-XXXXX |
| Condenser | WATERCOOLEDSHELLTUBE | CND-XXXXX |
| Condenser | WATERCOOLEDTUBEINTUBE | CND-XXXXX |
| Controller | FLOATING | CRL-XXXXX |
| Controller | PROPORTIONAL | CRL-XXXXX |
| Controller | PROPORTIONALINTEGRAL | CRL-XXXXX |
| Controller | PROPORTIONALINTEGRALDERIVATIVE | CRL-XXXXX |
| Controller | TWOPOSITION | CRL-XXXXX |
| Controller | USERDEFINED | LCM-XXXXX (Lighting Control Module) LCMD-XXXXX (Dimmable Lighting Control Module) |
| Controller | TIMEDTWOPOSITION | CRL-XXXXX |
| Cooled Beam | ACTIVE | CBM-XXXXX |
| Cooled Beam | PASSIVE | CBM-XXXXX |
| Cooled Beam | USERDEFINED | CBM-XXXXX |
| Cooling Tower | MECHANICALFORCEDDRAFT | CTR-XXXXX |
| Cooling Tower | MECHANICALINDUCEDDRAFT | CTR-XXXXX |
| Cooling Tower | NATURALDRAFT | CTR-XXXXX |
| Cooling Tower | USERDEFINED | CTR-XXXXX |
| Covering | CEILING | n/a |
| Covering | CLADDING | n/a |
| Covering | FLOORING | n/a |
| Covering | INSULATION | n/a |
| Covering | MEMBRANE | n/a |
| Covering | ROOFING | n/a |
| Covering | SLEEVING | n/a |
| Covering | USERDEFINED | n/a |
| Covering | WRAPPING | n/a |
| Curtain Wall | USERDEFINED | n/a |
| Damper | BACKDRAFTDAMPER | DMP-XXXXX |
| Damper | BALANCINGDAMPER | DMP-XXXXX |
| Damper | BLASTDAMPER | DMP-XXXXX |
| Damper | CONTROLDAMPER | CAV-XXXXX (Constant Air Volume) MLO-XXXXX (Louvre/Motorised) MLH-XXXXX (Louvre/Motorised with Integral LTHW Coil) VAV-XXXXX (Variable Air Volume) |
| Damper | FIREDAMPER | FDM-XXXXX |
| Damper | FIRESMOKEDAMPER | FSD-XXXXX |
| Damper | FUMEHOODEXHAUST | DMP-XXXXX |
| Damper | GRAVITYDAMPER | DMP-XXXXX |
| Damper | GRAVITYRELIEFDAMPER | DMP-XXXXX |
| Damper | RELIEFDAMPER | DMP-XXXXX |
| Damper | SMOKEDAMPER | SMD-XXXXX MSD-XXXXX (Motorised) |
| Damper | USERDEFINED | DMP-XXXXX |
| Discrete Accessory | n/a | DAC-XXXXX |
| Distribution Chamber Element | FORMEDDUCT | DCE-XXXXX |
| Distribution Chamber Element | INSPECTIONCHAMBER | DCE-XXXXX |
| Distribution Chamber Element | INSPECTIONPIT | DCE-XXXXX |
| Distribution Chamber Element | MANHOLE | DCE-XXXXX |
| Distribution Chamber Element | METERCHAMBER | DCE-XXXXX |
| Distribution Chamber Element | SUMP | DCE-XXXXX |
| Distribution Chamber Element | TRENCH | DCE-XXXXX |
| Distribution Chamber Element | USERDEFINED | DCE-XXXXX |
| Distribution Chamber Element | VALVECHAMBER | DCE-XXXXX |
| Door | n/a | [Space Name]-DXX (Door) AH-XXXXX (Access Hatch) |
| Duct Fitting | BEND | n/a |
| Duct Fitting | CONNECTOR | n/a |
| Duct Fitting | ENTRY | n/a |
| Duct Fitting | EXIT | n/a |
| Duct Fitting | JUNCTION | n/a |
| Duct Fitting | OBSTRUCTION | n/a |
| Duct Fitting | TRANSITION | n/a |
| Duct Fitting | USERDEFINED | n/a |
| Duct Segment | FLEXIBLESEGMENT | n/a |
| Duct Segment | RIGIDSEGMENT | n/a |
| Duct Segment | USERDEFINED | n/a |
| Duct Silencer | FLATOVAL | ATT-XXXXX (Attenuator) |
| Duct Silencer | RECTANGULAR | ATT-XXXXX (Attenuator) |
| Duct Silencer | ROUND | ATT-XXXXX (Attenuator) |
| Duct Silencer | USERDEFINED | ATT-XXXXX (Attenuator) |
| Electric Appliance | COMPUTER | EAP-XXXXX |
| Electric Appliance | DIRECTWATERHEATER | EAP-XXXXX |
| Electric Appliance | DISHWASHER | EAP-XXXXX |
| Electric Appliance | ELECTRICCOOKER | EAP-XXXXX |
| Electric Appliance | ELECTRICHEATER | EAP-XXXXX |
| Electric Appliance | FACSIMILE | EAP-XXXXX |
| Electric Appliance | FREESTANDINGFAN | EAP-XXXXX |
| Electric Appliance | FREEZER | EAP-XXXXX |
| Electric Appliance | FRIDGE_FREEZER | EAP-XXXXX |
| Electric Appliance | HANDDRYER | EAP-XXXXX |
| Electric Appliance | INDIRECTWATERHEATER | EAP-XXXXX |
| Electric Appliance | MICROWAVE | EAP-XXXXX |
| Electric Appliance | PHOTOCOPIER | EAP-XXXXX |
| Electric Appliance | PRINTER | EAP-XXXXX |
| Electric Appliance | RADIANTHEATER | ERP-XXXXX |
| Electric Appliance | REFRIGERATOR | EAP-XXXXX |
| Electric Appliance | SCANNER | EAP-XXXXX |
| Electric Appliance | TELEPHONE | EAP-XXXXX |
| Electric Appliance | TUMBLEDRYER | EAP-XXXXX |
| Electric Appliance | TV | EAP-XXXXX |
| Electric Appliance | USERDEFINED | EAP-XXXXX |
| Electric Appliance | VENDINGMACHINE | EAP-XXXXX |
| Electric Appliance | WASHINGMACHINE | EAP-XXXXX |
| Electric Appliance | WATERCOOLER | EAP-XXXXX |
| Electric Appliance | WATERHEATER | WHR-XXXX (Water Heater) LWH-XXXXX (Local Water Heater) |
| Electric Distribution Point | ALARMPANEL | EPB-XXXXX |
| Electric Distribution Point | CONSUMERUNIT | EDP-XXXXX |
| Electric Distribution Point | CONTROLPANEL | MCP-XXXXX (Mechanical Control Panel) |
| Electric Distribution Point | DISTRIBUTIONBOARD | EDB-XXXXX (Distribution Board) ELB-XXXXX (Lighting Distribution Board) EPB-XXXXX (Power Distribution Board) |
| Electric Distribution Point | GASDETECTORPANEL | EPB-XXXXX |
| Electric Distribution Point | MIMICPANEL | EPB-XXXXX |
| Electric Distribution Point | MOTORCONTROLCENTRE | EDP-XXXXX |
| Electric Distribution Point | SWITCHBOARD | EDP-XXXXX |
| Electric Distribution Point | USERDEFINED | EDP-XXXXX |
| Electric Flow Storage Device | BATTERY | EHB-XXXXX (Electric Heater Battery) |
| Electric Flow Storage Device | CAPACITORBANK | EFS-XXXXX |
| Electric Flow Storage Device | HARMONICFILTER | EFS-XXXXX |
| Electric Flow Storage Device | UPS | UPS-XXXXX |
| Electric Flow Storage Device | USERDEFINED | EFS-XXXXX |
| Electric Generator | USERDEFINED | G-XXXXX |
| Electric Heater | ELECTRICCABLEHEATER | EHT-XXXXX |
| Electric Heater | ELECTRICMATHEATER | EHT-XXXXX |
| Electric Heater | ELECTRICPOINTHEATER | EHT-XXXXX |
| Electric Heater | USERDEFINED | THR-XXXXX (Trench Heater) |
| Electric Motor | DC | EMT-XXXXX |
| Electric Motor | INDUCTION | EMT-XXXXX |
| Electric Motor | POLYPHASE | EMT-XXXXX |
| Electric Motor | RELUCTANCESYNCHRONOUS | EMT-XXXXX |
| Electric Motor | SYNCHRONOUS | EMT-XXXXX |
| Electric Motor | USERDEFINED | EMT-XXXXX |
| Electric Time Control | RELAY | ETC-XXXXX |
| Electric Time Control | TIMECLOCK | ETC-XXXXX |
| Electric Time Control | TIMEDELAY | ETC-XXXXX |
| Electric Time Control | USERDEFINED | ETC-XXXXX |
| Element Assembly | ACCESSORY_ASSEMBLY | n/a |
| Element Assembly | ARCH | n/a |
| Element Assembly | BEAM_GRID | n/a |
| Element Assembly | BRACED_FRAME | n/a |
| Element Assembly | GIRDER | n/a |
| Element Assembly | REINFORCEMENT_UNIT | n/a |
| Element Assembly | RIGID_FRAME | n/a |
| Element Assembly | SLAB_FIELD | n/a |
| Element Assembly | TRUSS | n/a |
| Element Assembly | USERDEFINED | n/a |
| Evaporative Cooler | DIRECTEVAPORATIVEAIRWASHER | ECL-XXXXX |
| Evaporative Cooler | DIRECTEVAPORATIVEPACKAGEDROTARYAIRCOOLER | ECL-XXXXX |
| Evaporative Cooler | DIRECTEVAPORATIVERANDOMMEDIAAIRCOOLER | ECL-XXXXX |
| Evaporative Cooler | DIRECTEVAPORATIVERIGIDMEDIAAIRCOOLER | ECL-XXXXX |
| Evaporative Cooler | DIRECTEVAPORATIVESLINGERSPACKAGEDAIRCOOLER | ECL-XXXXX |
| Evaporative Cooler | INDIRECTDIRECTCOMBINATION | ECL-XXXXX |
| Evaporative Cooler | INDIRECTEVAPORATIVECOOLINGTOWERORCOILCOOLER | ECL-XXXXX |
| Evaporative Cooler | INDIRECTEVAPORATIVEPACKAGEAIRCOOLER | ECL-XXXXX |
| Evaporative Cooler | INDIRECTEVAPORATIVEWETCOIL | ECL-XXXXX |
| Evaporative Cooler | USERDEFINED | ECL-XXXXX |
| Evaporator | DIRECTEXPANSIONBRAZEDPLATE | EVP-XXXXX |
| Evaporator | DIRECTEXPANSIONSHELLANDTUBE | EVP-XXXXX |
| Evaporator | DIRECTEXPANSIONTUBEINTUBE | EVP-XXXXX |
| Evaporator | FLOODEDSHELLANDTUBE | EVP-XXXXX |
| Evaporator | SHELLANDCOIL | EVP-XXXXX |
| Evaporator | USERDEFINED | EVP-XXXXX |
| Fan | CENTRIFUGALAIRFOIL | EFN-XXXXX (Extract) SFN-XXXXX (Supply) |
| Fan | CENTRIFUGALBACKWARDINCLINEDCURVED | EFN-XXXXX (Extract) SFN-XXXXX (Supply) |
| Fan | CENTRIFUGALFORWARDCURVED | EFN-XXXXX (Extract) SFN-XXXXX (Supply) |
| Fan | CENTRIFUGALRADIAL | EFN-XXXXX (Extract) SFN-XXXXX (Supply) |
| Fan | PROPELLORAXIAL | EFN-XXXXX (Extract) SFN-XXXXX (Supply) |
| Fan | TUBEAXIAL | EFN-XXXXX (Extract) SFN-XXXXX (Supply) |
| Fan | USERDEFINED | EFN-XXXXX (Extract) SFN-XXXXX (Supply) |
| Fan | VANEAXIAL | EFN-XXXXX (Extract) SFN-XXXXX (Supply) |
| Fastener | n/a | n/a |
| Filter | AIRPARTICLEFILTER | APF-XXXXX (Air and Dirt Separator) |
| Filter | ODORFILTER | FLT-XXXXX |
| Filter | OILFILTER | FLT-XXXXX |
| Filter | STRAINER | FLT-XXXXX |
| Filter | USERDEFINED | FLT-XXXXX |
| Filter | WATERFILTER | WFT-XXXXX (X-Pot) |
| Fire Suppression Terminal | BREECHINGINLET | FST-XXXXX |
| Fire Suppression Terminal | FIREHYDRANT | FST-XXXXX |
| Fire Suppression Terminal | HOSEREEL | FST-XXXXX |
| Fire Suppression Terminal | SPRINKLER | FST-XXXXX |
| Fire Suppression Terminal | SPRINKLERDEFLECTOR | FST-XXXXX |
| Fire Suppression Terminal | USERDEFINED | FST-XXXXX |
| Flow Instrument | AMMETER | FIN-XXXXX |
| Flow Instrument | FREQUENCYMETER | FIN-XXXXX |
| Flow Instrument | PHASEANGLEMETER | FIN-XXXXX |
| Flow Instrument | POWERFACTORMETER | FIN-XXXXX |
| Flow Instrument | PRESSUREGAUGE | FIN-XXXXX |
| Flow Instrument | THERMOMETER | FIN-XXXXX |
| Flow Instrument | USERDEFINED | FIN-XXXXX |
| Flow Instrument | VOLTMETER_PEAK | FIN-XXXXX |
| Flow Instrument | VOLTMETER_RMS | FIN-XXXXX |
| Flow Meter | ELECTRICMETER | FMT-XXXXX |
| Flow Meter | ENERGYMETER | FMT-XXXXX |
| Flow Meter | FLOWMETER | FMT-XXXXX |
| Flow Meter | GASMETER | GMT-XXXXX |
| Flow Meter | OILMETER | FMT-XXXXX |
| Flow Meter | USERDEFINED | HMT-XXXXX (Heat Meter) |
| Flow Meter | WATERMETER | WMT-XXXXX |
| Footing | FOOTING_BEAM | n/a |
| Footing | PAD_FOOTING | n/a |
| Footing | PILE_CAP | n/a |
| Footing | STRIP_FOOTING | n/a |
| Footing | USERDEFINED | n/a |
| Furniture | n/a | FRN-XXXXX |
| Gas Terminal | GASAPPLIANCE | GTM-XXXXX |
| Gas Terminal | GASBOOSTER | BSR-XXXXX |
| Gas Terminal | GASBURNER | GTM-XXXXX |
| Gas Terminal | USERDEFINED | GRH-XXXXX (Gas-Fired Radiant Heater) |
| Heat Exchanger | PLATE | HEP-XXXXX |
| Heat Exchanger | SHELLANDTUBE | HEX-XXXXX |
| Heat Exchanger | USERDEFINED | HEX-XXXXX |
| Humidifier | ADIABATICAIRWASHER | HUM-XXXXX |
| Humidifier | ADIABATICATOMIZING | HUM-XXXXX |
| Humidifier | ADIABATICCOMPRESSEDAIRNOZZLE | HUM-XXXXX |
| Humidifier | ADIABATICPAN | HUM-XXXXX |
| Humidifier | ADIABATICRIGIDMEDIA | HUM-XXXXX |
| Humidifier | ADIABATICULTRASONIC | HUM-XXXXX |
| Humidifier | ADIABATICWETTEDELEMENT | HUM-XXXXX |
| Humidifier | ASSISTEDBUTANE | HUM-XXXXX |
| Humidifier | ASSISTEDELECTRIC | HUM-XXXXX |
| Humidifier | ASSISTEDNATURALGAS | HUM-XXXXX |
| Humidifier | ASSISTEDPROPANE | HUM-XXXXX |
| Humidifier | ASSISTEDSTEAM | HUM-XXXXX |
| Humidifier | STEAMINJECTION | HUM-XXXXX |
| Humidifier | USERDEFINED | HUM-XXXXX |
| Junction Box | USERDEFINED | n/a |
| Lamp | COMPACTFLUORESCENT | n/a |
| Lamp | FLUORESCENT | n/a |
| Lamp | HIGHPRESSUREMERCURY | n/a |
| Lamp | HIGHPRESSURESODIUM | n/a |
| Lamp | METALHALIDE | n/a |
| Lamp | TUNGSTENFILAMENT | n/a |
| Lamp | USERDEFINED | n/a |
| Light Fixture | DIRECTIONSOURCE | LFT-XXXXX |
| Light Fixture | POINTSOURCE | LFT-XXXXX |
| Light Fixture | USERDEFINED | LFT-XXXXX |
| Mechanical Fastener | n/a | n/a |
| Member | BRACE | n/a |
| Member | CHORD | n/a |
| Member | COLLAR | n/a |
| Member | MEMBER | n/a |
| Member | MULLION | n/a |
| Member | PLATE | n/a |
| Member | POST | n/a |
| Member | PURLIN | n/a |
| Member | RAFTER | n/a |
| Member | STRINGER | n/a |
| Member | STRUT | n/a |
| Member | STUD | n/a |
| Member | USERDEFINED | n/a |
| Motor Connection | BELTDRIVE | MCN-XXXXX |
| Motor Connection | COUPLING | MCN-XXXXX |
| Motor Connection | DIRECTDRIVE | MCN-XXXXX |
| Motor Connection | USERDEFINED | MCN-XXXXX |
| Outlet | AUDIOVISUALOUTLET | OUT-XXXXX |
| Outlet | COMMUNICATIONSOUTLET | OUT-XXXXX |
| Outlet | POWEROUTLET | OUT-XXXXX |
| Outlet | USERDEFINED | OUT-XXXXX |
| Pile | COHESION | n/a |
| Pile | FRICTION | n/a |
| Pile | SUPPORT | n/a |
| Pile | USERDEFINED | n/a |
| Pile | DRIVEN | n/a |
| Pipe Fitting | BEND | n/a |
| Pipe Fitting | CONNECTOR | n/a |
| Pipe Fitting | ENTRY | n/a |
| Pipe Fitting | EXIT | n/a |
| Pipe Fitting | JUNCTION | n/a |
| Pipe Fitting | OBSTRUCTION | n/a |
| Pipe Fitting | TRANSITION | n/a |
| Pipe Fitting | USERDEFINED | n/a |
| Pipe Segment | FLEXIBLESEGMENT | n/a |
| Pipe Segment | GUTTER | n/a |
| Pipe Segment | RIGIDSEGMENT | FWS-XXXXX (Foul Water Stack) SWS-XXXXX (Surface Water Stack) |
| Pipe Segment | SPOOL | n/a |
| Pipe Segment | USERDEFINED | n/a |
| Plate | CURTAIN_PANEL | n/a |
| Plate | SHEET | n/a |
| Plate | USERDEFINED | n/a |
| Protective Device | CIRCUITBREAKER | PDV-XXXXX |
| Protective Device | FUSEDISCONNECTOR | PDV-XXXXX |
| Protective Device | RESIDUALCURRENTCIRCUITBREAKER | PDV-XXXXX |
| Protective Device | RESIDUALCURRENTSWITCH | PDV-XXXXX |
| Protective Device | USERDEFINED | PDV-XXXXX |
| Protective Device | VARISTOR | PDV-XXXXX |
| Protective Device | EARTHFAILUREDEVICE | PDV-XXXXX |
| Pump | CIRCULATOR | PMP-XXXXX |
| Pump | ENDSUCTION | PMP-XXXXX |
| Pump | SPLITCASE | PMP-XXXXX |
| Pump | USERDEFINED | PMP-XXXXX |
| Pump | VERTICALINLINE | PMP-XXXXX |
| Pump | VERTICALTURBINE | PMP-XXXXX |
| Railing | BALUSTRADE | n/a |
| Railing | GUARDRAIL | n/a |
| Railing | HANDRAIL | n/a |
| Railing | USERDEFINED | n/a |
| Ramp | HALF_TURN_RAMP | n/a |
| Ramp | QUARTER_TURN_RAMP | n/a |
| Ramp | SPIRAL_RAMP | n/a |
| Ramp | STRAIGHT_RUN_RAMP | n/a |
| Ramp | TWO_QUARTER_TURN_RAMP | n/a |
| Ramp | TWO_STRAIGHT_RUN_RAMP | n/a |
| Ramp | USERDEFINED | n/a |
| Ramp Flight | SPIRAL | n/a |
| Ramp Flight | STRAIGHT | n/a |
| Ramp Flight | USERDEFINED | n/a |
| Reinforcing Bar | EDGE | n/a |
| Reinforcing Bar | LIGATURE | n/a |
| Reinforcing Bar | MAIN | n/a |
| Reinforcing Bar | PUNCHING | n/a |
| Reinforcing Bar | RING | n/a |
| Reinforcing Bar | SHEAR | n/a |
| Reinforcing Bar | STUD | n/a |
| Reinforcing Bar | USERDEFINED | n/a |
| Reinforcing Mesh | n/a | n/a |
| Roof | BARREL_ROOF | n/a |
| Roof | BUTTERFLY_ROOF | n/a |
| Roof | DOME_ROOF | n/a |
| Roof | FLAT_ROOF | n/a |
| Roof | FREEFORM | n/a |
| Roof | GABLE_ROOF | n/a |
| Roof | GAMBREL_ROOF | n/a |
| Roof | HIP_ROOF | n/a |
| Roof | HIPPED_GABLE_ROOF | n/a |
| Roof | MANSARD_ROOF | n/a |
| Roof | PAVILION_ROOF | n/a |
| Roof | RAINBOW_ROOF | n/a |
| Roof | SHED_ROOF | n/a |
| Roof | USERDEFINED | n/a |
| Sanitary Terminal | BATH | SAN-XXXXX |
| Sanitary Terminal | BIDET | SAN-XXXXX |
| Sanitary Terminal | CISTERN | SAN-XXXXX |
| Sanitary Terminal | SANITARYFOUNTAIN | SAN-XXXXX |
| Sanitary Terminal | SHOWER | SAN-XXXXX |
| Sanitary Terminal | SINK | SAN-XXXXX |
| Sanitary Terminal | TOILETPAN | SAN-XXXXX |
| Sanitary Terminal | URINAL | SAN-XXXXX |
| Sanitary Terminal | USERDEFINED | SAN-XXXXX |
| Sanitary Terminal | WASHHANDBASIN | SAN-XXXXX |
| Sanitary Terminal | WCSEAT | SAN-XXXXX |
| Sensor | CO2SENSOR | SNS-XXXXX |
| Sensor | FIRESENSOR | SNS-XXXXX |
| Sensor | FLOWSENSOR | SNS-XXXXX |
| Sensor | GASSENSOR | SNS-XXXXX |
| Sensor | HEATSENSOR | SNS-XXXXX |
| Sensor | HUMIDITYSENSOR | SNS-XXXXX |
| Sensor | LIGHTSENSOR | SNS-XXXXX |
| Sensor | MOISTURESENSOR | SNS-XXXXX |
| Sensor | MOVEMENTSENSOR | SNS-XXXXX |
| Sensor | PRESSURESENSOR | SNS-XXXXX |
| Sensor | SMOKESENSOR | SNS-XXXXX |
| Sensor | SOUNDSENSOR | SNS-XXXXX |
| Sensor | TEMPERATURESENSOR | SNS-XXXXX |
| Sensor | USERDEFINED | LDS-XXXXX (Leak Detection Sensor) |
| Slab | BASESLAB | n/a |
| Slab | FLOOR | n/a |
| Slab | LANDING | n/a |
| Slab | ROOF | n/a |
| Slab | USERDEFINED | n/a |
| Space Heater | CONVECTOR | SCH-XXXXX (Fan Convector) |
| Space Heater | USERDEFINED | SPH-XXXXX |
| Space Heater | BASEBOARDHEATER | SPH-XXXXX |
| Space Heater | FINNEDTUBEUNIT | SPH-XXXXX |
| Space Heater | PANELRADIATOR | SRH-XXXXX |
| Space Heater | SECTIONALRADIATOR | SRH-XXXXX |
| Space Heater | TUBULARRADIATOR | SRH-XXXXX |
| Space Heater | UNITHEATER | SUH-XXXXX (LTHW) SGH-XXXXX (Gas-Fired) |
| Stack Terminal | BIRDCAGE | STM-XXXXX |
| Stack Terminal | COWL | RCW-XXXXX |
| Stack Terminal | RAINWATERHOPPER | STM-XXXXX |
| Stack Terminal | USERDEFINED | STM-XXXXX |
| Stair | CURVED_RUN_STAIR | n/a |
| Stair | DOUBLE_RETURN_STAIR | n/a |
| Stair | HALF_TURN_STAIR | n/a |
| Stair | HALF_WINDING_STAIR | n/a |
| Stair | QUARTER_TURN_STAIR | n/a |
| Stair | QUARTER_WINDING_STAIR | n/a |
| Stair | SPIRAL_STAIR | n/a |
| Stair | STRAIGHT_RUN_STAIR | n/a |
| Stair | THREE_QUARTER_TURN_STAIR | n/a |
| Stair | THREE_QUARTER_WINDING_STAIR | n/a |
| Stair | TWO_CURVED_RUN_STAIR | n/a |
| Stair | TWO_QUARTER_TURN_STAIR | n/a |
| Stair | TWO_QUARTER_WINDING_STAIR | n/a |
| Stair | TWO_STRAIGHT_RUN_STAIR | n/a |
| Stair | USERDEFINED | n/a |
| Stair Flight | CURVED | n/a |
| Stair Flight | FREEFORM | n/a |
| Stair Flight | SPIRAL | n/a |
| Stair Flight | STRAIGHT | n/a |
| Stair Flight | USERDEFINED | n/a |
| Stair Flight | WINDER | n/a |
| Switching Device | CONTACTOR | SWD-XXXXX |
| Switching Device | EMERGENCYSTOP | SWD-XXXXX |
| Switching Device | STARTER | SWD-XXXXX |
| Switching Device | SWITCHDISCONNECTOR | SWD-XXXXX |
| Switching Device | TOGGLESWITCH | SWD-XXXXX |
| Switching Device | USERDEFINED | SWD-XXXXX |
| System Furniture Element | n/a | SFE-XXXXX |
| Tank | EXPANSION | EVL-XXXXX (Expansion Vessel) |
| Tank | PREFORMED | CWT-XXXXX (Cold Water Storage) |
| Tank | PRESSUREVESSEL | PUT-XXXXX (Pressurisation Unit) |
| Tank | SECTIONAL | CWT-XXXXX (Cold Water Storage) |
| Tank | USERDEFINED | BVL-XXXXX (Buffer Vessel) TSR-XXXXX (Thermal Store) |
| Tendon | BAR | n/a |
| Tendon | COATED | n/a |
| Tendon | STRAND | n/a |
| Tendon | USERDEFINED | n/a |
| Tendon | WIRE | n/a |
| Tendon Anchor | n/a | n/a |
| Transformer | CURRENT | TRF-XXXXX |
| Transformer | FREQUENCY | TRF-XXXXX |
| Transformer | USERDEFINED | TRF-XXXXX |
| Transformer | VOLTAGE | TRF-XXXXX |
| Transport Element | ELEVATOR | ELE-XXXXX |
| Transport Element | ESCALATOR | ESC-XXXXX |
| Transport Element | MOVINGWALKWAY | MOV-XXXXX |
| Transport Element | USERDEFINED | TRE-XXXXX |
| Tube Bundle | FINNED | TBN-XXXXX |
| Tube Bundle | USERDEFINED | TBN-XXXXX |
| Unitary Equipment | AIRCONDITIONINGUNIT | IAC-XXXXX (Indoor) OAC-XXXXX (Outdoor) |
| Unitary Equipment | AIRHANDLER | AHU-XXXXX |
| Unitary Equipment | ROOFTOPUNIT | UEQ-XXXXX |
| Unitary Equipment | SPLITSYSTEM | UEQ-XXXXX |
| Unitary Equipment | USERDEFINED | UEQ-XXXXX |
| Valve | AIRRELEASE | VLV-XXXXX |
| Valve | ANTIVACUUM | VLV-XXXXX |
| Valve | CHANGEOVER | VLV-XXXXX |
| Valve | CHECK | VLV-XXXXX |
| Valve | COMMISSIONING | VLV-XXXXX |
| Valve | DIVERTING | VLV-XXXXX |
| Valve | DOUBLECHECK | VLV-XXXXX |
| Valve | DOUBLEREGULATING | VLV-XXXXX |
| Valve | DRAWOFFCOCK | VLV-XXXXX |
| Valve | FAUCET | VLV-XXXXX |
| Valve | FLUSHING | VLV-XXXXX |
| Valve | GASCOCK | GSV-XXXXX (Gas Solenoid Value) |
| Valve | GASTAP | GSV-XXXXX (Gas Solenoid Value) |
| Valve | ISOLATING | VLV-XXXXX |
| Valve | MIXING | VLV-XXXXX |
| Valve | PRESSUREREDUCING | VLV-XXXXX |
| Valve | PRESSURERELIEF | VLV-XXXXX |
| Valve | REGULATING | VLV-XXXXX |
| Valve | SAFETYCUTOFF | VLV-XXXXX |
| Valve | STEAMTRAP | VLV-XXXXX |
| Valve | STOPCOCK | VLV-XXXXX |
| Valve | USERDEFINED | VLV-XXXXX |
| Vibration Isolator | COMPRESSION | VIB-XXXXX |
| Vibration Isolator | SPRING | VIB-XXXXX |
| Vibration Isolator | USERDEFINED | VIB-XXXXX |
| Wall | ELEMENTEDWALL | n/a |
| Wall | PLUMBINGWALL | n/a |
| Wall | POLYGONAL | n/a |
| Wall | SHEAR | n/a |
| Wall | STANDARD | n/a |
| Wall | USERDEFINED | n/a |
| Waste Terminal | FLOORTRAP | WTM-XXXXX |
| Waste Terminal | FLOORWASTE | WTM-XXXXX |
| Waste Terminal | GREASEINTERCEPTOR | WTM-XXXXX |
| Waste Terminal | GULLYSUMP | WTM-XXXXX |
| Waste Terminal | GULLYTRAP | WTM-XXXXX |
| Waste Terminal | OILINTERCEPTOR | WTM-XXXXX |
| Waste Terminal | PETROLINTERCEPTOR | WTM-XXXXX |
| Waste Terminal | ROOFDRAIN | WTM-XXXXX |
| Waste Terminal | USERDEFINED | WTM-XXXXX |
| Waste Terminal | WASTEDISPOSALUNIT | WTM-XXXXX |
| Waste Terminal | WASTETRAP | WTM-XXXXX |
| Window | n/a | [Space Name]-WXX |

Object occurrence nomenclature shall adhere to the following:

all Xs are replaced by numbers

the list provided in this section aligns with the entities and enumerations (predefined types) set out in the Detailed Exchange Information Requirements. Whilst it is acceptable to propose alternatives to the name format, the list of entities and enumerations shall not be amended

multiple name formats are allowable for the same entity and enumeration, if required

this list of entities, enumeration types (predefined types) and associated object occurrence naming would need to be amended where ISO 16739-1:2024 (IFC4.3 ADD2) is proposed in lieu of PAS/ISO 16739:2005 (IFC2x3 TC1)

if preferred, the naming format may also include additional metadata to help distinguish further or reduce conflict between Disciplines. For example, Names could also include the Space name and/or Discipline code. The Name format shall be updated accordingly to reflect this

### 5.2.9 System nomenclature

This section sets out the system nomenclature for assets.

The system names shall populate information required by the COBie System workbook. Names and Descriptions shall therefore align to the nomenclature requirements set out in this section of the resource.

This list is developed from the Predefined Types for IfcDistributionSystem entities published as part of the IFC4.3 ADD2 (ISO 16739-1:2024) schema.

Classifications (COBie Category) associated to systems shall be taken from the Uniclass Ss Systems table. The Category column in the table below has been provided for each system enumeration as a guide. The project shall use the version of the Uniclass Ss Systems table stated in 4.5.1 Asset classification.

Where a system name listed is not appropriate then a user defined value shall be used as required. Additional system naming requirements shall be provided within the (pre-appointment) BIM Execution Plan.

| Name | Description | Category |
| --- | --- | --- |
| AirConditioning_SystemXX | Conditioned air distribution system for purposes of maintaining a temperature range within one or more spaces | Refer to codes provided under: Ss_65_80: Air conditioning systems Ss_15_95_65: Temporary ventilation and air conditioning systems |
| Audiovisual_SystemXX | A transport of a single media source, having audio and/or video streams | Refer to codes provided under: Ss_75_10: Communications systems Ss_15_95_75: Temporary communications, security, safety, control and protection systems |
| Catenary_SystemXX | A longitudinal distribution system that supports contact wires, including catenary wire droppers and stich wires | n/a |
| Chemical_SystemXX | Arbitrary chemical further qualified by property set, such as for medical or industrial use | Refer to codes provided under: Ss_50_75: Wastewater storage, treatment and disposal systems Ss_55_60: Process liquid distribution and supply systems Ss_55_70: Water distribution and supply systems Ss_15_95_55: Temporary piped supply systems |
| ChilledWater_SystemXX | Nonpotable chilled water, such as circulated through an evaporator | Refer to codes provided under: Ss_60_40: Space heating and cooling systems Ss_15_95_60: Temporary heating, cooling and refrigeration systems |
| Communication_SystemXX | Communication system | Refer to codes provided under: Ss_75_10: Communications systems Ss_15_95_75: Temporary communications, security, safety, control and protection systems |
| CompressedAir_SystemXX | Compressed air system | Refer to codes provided under: Ss_55_20: Gas and vacuum distribution and supply systems Ss_15_95_55: Temporary piped supply systems |
| CondenserWater_SystemXX | Nonpotable water, such as circulated through a condenser | Refer to codes provided under: Ss_55_40: Steam distribution and supply systems Ss_15_95_55: Temporary piped supply systems |
| Control_SystemXX | A transport or network dedicated to control system usage | Refer to codes provided under: Ss_75_70: Control and management systems Ss_15_95_75: Temporary communications, security, safety, control and protection systems |
| Conveying_SystemXX | Arbitrary supply of substances | As required |
| Data_SystemXX | A network having general-purpose usage | Refer to codes provided under: Ss_75_10: Communications systems Ss_15_95_75: Temporary communications, security, safety, control and protection systems |
| Disposal_SystemXX | Arbitrary disposal of substances | Refer to codes provided under: Ss_50_10: Gas waste collection and distribution systems Ss_50_20: Non-aqueous liquid waste collection and distribution systems Ss_50_40: Solid waste collection and distribution systems Ss_50_50: Gas waste storage, treatment and disposal systems Ss_50_60: Non-aqueous liquid waste storage, treatment and disposal systems Ss_50_70: Drainage storage, treatment and disposal systems Ss_50_75: Wastewater storage, treatment and disposal systems Ss_50_80: Solid waste storage, treatment and disposal systems Ss_15_95_50: Temporary disposal systems |
| DomesticColdWater_SystemXX | Unheated potable water distribution system | Refer to codes provided under: Ss_55_70: Water distribution and supply systems Ss_15_95_55: Temporary piped supply systems |
| DomesticHotWater_SystemXX | Heated potable water distribution system | Refer to codes provided under: Ss_55_70: Water distribution and supply systems Ss_15_95_55: Temporary piped supply systems Ss_60_40: Space heating and cooling systems Ss_15_95_60: Temporary heating, cooling and refrigeration systems |
| Drainage_SystemXX | Drainage collection system | Refer to codes provided under: Ss_50_35: Wastewater collection systems Ss_15_95_50: Temporary disposal systems |
| Earthing_SystemXX | A path for equipotential bonding, conducting current to the ground | Refer to codes provided under: Ss_70_30: Electricity distribution systems Ss_15_95_70: Temporary electrical systems |
| Electrical_SystemXX | A circuit for delivering electrical power | Refer to codes provided under: Ss_70_10: Electrical power generation systems Ss_70_30: Electricity distribution systems Ss_15_95_70: Temporary electrical systems |
| Electroacoustic_SystemXX | An amplified audio signal such as for loudspeakers | Refer to codes provided under: Ss_75_10: Communications systems Ss_15_95_75: Temporary communications, security, safety, control and protection systems |
| Exhaust_SystemXX | Exhaust air collection system for removing stale or noxious air from one or more spaces | Refer to codes provided under: Ss_65_40: Ventilation systems Ss_65_60: Specialist ventilation systems Ss_15_95_65: Temporary ventilation and air conditioning systems |
| FireProtection_SystemXX | Fire protection sprinkler system | Refer to codes provided under: Ss_55_30: Fire-extinguishing systems Ss_15_95_55: Temporary piped supply systems |
| FixedTransmissionNetwork_SystemXX | Represents all wired networks that provide a data transmission channel using optical fibre cables, copper cables or both. It aggregates many technologies that are based on the multiplexing method | n/a |
| Fuel_SystemXX | Arbitrary supply of fuel | Refer to codes provided under: Ss_50_60: Non-aqueous liquid waste storage, treatment and disposal systems Ss_15_95_50: Temporary disposal systems Ss_55_10: Liquid fuel extraction, treatment and storage systems Ss_55_20: Gas and vacuum distribution and supply systems Ss_55_50: Liquid fuel distribution and supply systems Ss_15_95_55: Temporary piped supply systems |
| Gas_SystemXX | Gas-phase materials such as methane or natural gas | Refer to codes provided under: Ss_50_10: Gas waste collection and distribution systems Ss_55_05: Gas extraction, treatment and storage systems Ss_55_20: Gas and vacuum distribution and supply systems |
| Hazardous_SystemXX | Hazardous material or fluid collection system | Refer to codes provided under: Ss_65_40: Ventilation systems Ss_65_60: Specialist ventilation systems Ss_15_95_65: Temporary ventilation and air conditioning systems |
| Heating_SystemXX | Water or steam heated from a boiler and circulated through radiators | Refer to codes provided under: Ss_60_40: Space heating and cooling systems Ss_15_95_60: Temporary heating, cooling and refrigeration systems |
| Lighting_SystemXX | A circuit dedicated for lighting, such as a fixture having sockets for lamps | Refer to codes provided under: Ss_70_80: Lighting systems Ss_15_95_70: Temporary electrical systems |
| LightningProtection_SystemXX | A path for conducting lightning current to the ground | Refer to codes provided under: Ss_75_50: Safety and protection systems Ss_15_95_75: Temporary communications, security, safety, control and protection systems |
| MobileNetwork_SystemXX | Mobile network insures wireless communication by providing a secure platform for voice and data communication between infrastructure operators, including drivers, dispatchers, shunting team members and station controllers | Refer to codes provided under: Ss_70_30_63: Mobile Communications Systems |
| Monitoring_SystemXX | Sensor-based system for building and infrastructure environmental monitoring and control | Refer to codes provided under: Ss_75_70: Monitoring Systems |
| MunicipalSolidWaste_SystemXX | Items consumed and discarded, commonly known as trash or garbage | Refer to codes provided under: Ss_50_40: Solid waste collection and distribution systems Ss_50_80: Solid waste storage, treatment and disposal systems Ss_15_95_50: Temporary disposal systems |
| Oil_SystemXX | Oil distribution system | Refer to codes provided under: Ss_55_50: Liquid fuel distribution and supply systems Ss_15_95_55: Temporary piped supply systems |
| Operation_SystemXX | Operating supplies system | As required |
| OperationalTelephony_SystemXX | A system that allows communications between operators (e.g., switchtender, traffic regulator, operational agents, etc) in operational centres and on the infrastructure site (e.g., railway, tunnel or road) | n/a |
| OverheadContactLine_SystemXX | An overhead contact line system above the upper limit of the train using an overhead contact line and a catenary system to supply current to traction units | n/a |
| PowerGeneration_SystemXX | A path for power generation | Refer to codes provided under: Ss_70_10: Electrical power generation systems Ss_15_95_70: Temporary electrical systems |
| Rainwater_SystemXX | Rainwater resulting from precipitation which directly falls on a parcel | Refer to codes provided under: Ss_50_30: Above-ground drainage collection systems Ss_50_35: Wastewater collection systems Ss_15_95_50: Temporary disposal systems |
| Refrigeration_SystemXX | Refrigerant distribution system for purposes of fulfilling all or parts of a refrigeration cycle | Refer to codes provided under: Ss_60_60: Refrigeration systems Ss_15_95_60: Temporary heating, cooling and refrigeration systems |
| ReturnCircuit_SystemXX | A distribution system which forms the intended path for the traction return current and the current under fault conditions | n/a |
| Security_SystemXX | A transport or network dedicated to security system usage | Refer to codes provided under: Ss_75_40: Security systems Ss_75_50: Safety and protection systems Ss_15_95_75: Temporary communications, security, safety, control and protection systems |
| Sewage_SystemXX | Sewage collection system | Refer to codes provided under: Ss_50_35: Wastewater collection systems Ss_15_95_50: Temporary disposal systems Ss_55_90: Piped solids distribution and supply systems Ss_15_95_55: Temporary piped supply systems |
| Signal_SystemXX | A raw analogue signal, such as modulated data or measurements from sensors | Refer to codes provided under: Ss_75_30: Signal systems Ss_15_95_75: Temporary communications, security, safety, control and protection systems |
| Stormwater_SystemXX | Stormwater resulting from precipitation which runs off or travels over the ground surface | Refer to: Ss_50_35: Wastewater collection systems Ss_15_95_50: Temporary disposal systems |
| Telephone_SystemXX | A transport or network dedicated to telephone system usage | Refer to: Ss_75_10: Communications systems Ss_15_95_75: Temporary communications, security, safety, control and protection systems |
| TV_SystemXX | A transport of multiple media sources such as analog cable TV, satellite TV, or over-the-air TV | Refer to: Ss_75_10: Communication systems Ss_15_95_75: Temporary communications, security, safety, control and protection systems |
| Vacuum_SystemXX | Vacuum distribution system | Refer to: Ss_55_20: Gas and vacuum distribution and supply systems Ss_15_95_55: Temporary piped supply systems |
| Vent_SystemXX | Vent system for wastewater piping systems | Refer to: Ss_50_35: Wastewater collection systems Ss_15_95_50: Temporary disposal systems Ss_55_70: Water distribution and supply systems Ss_15_95_55: Temporary piped supply systems |
| Ventilation_SystemXX | Ventilation air distribution system involved in either the exchange of air to the outside as well as circulation of air within a building | Refer to: Ss_65_40: Ventilation systems Ss_65_60: Specialist ventilation systems Ss_15_95_65: Temporary ventilation and air conditioning systems |
| Wastewater_SystemXX | Water adversely affected in quality by anthropogenic influence, possibly originating from sewage, drainage, or other source | Refer to: Ss_50_75: Wastewater storage, treatment and disposal systems Ss_15_95_50: Temporary disposal systems Ss_55_15: Water extraction, treatment and storage systems Ss_15_95_55: Temporary piped supply systems |
| WaterSupply_SystemXX | Arbitrary water supply | Refer to: Ss_55_70: Water distribution and supply systems Ss_15_95_55: Temporary piped supply systems Ss_75_70: Control and management systems Ss_15_95_75: Temporary communications, security, safety, control and protection systems |
| [UserDefined]_SystemXX | Other user defined system | As required |

All Xs are to be replaced by sequential numbers and can be increased to three digits if required.

### 5.2.10 COBie picklists

The following picklists are to be used for this project for the COBie output:

| Sheet | Column | Picklist | Values |
| --- | --- | --- | --- |
| Contact | Category | Category-Role | (from Uniclass Ro Roles) |
| Facility | Category | Category-Facility | (from Uniclass En Entities) |
| Facility | LinearUnits | LinearUnits | millimetres |
| Facility | AreaUnits | AreaUnits | squaremetres |
| Facility | VolumeUnits | VolumeUnits | cubicmetres |
| Facility | CurrencyUnit | CostUnit | pounds |
| Facility | Phase | Category-Phase | RIBA Stage 1: Preparation and Brief, RIBA Stage 2: Concept Design, RIBA Stage 3: Spatial Coordination, RIBA Stage 4: Technical Design, RIBA Stage 5: Construction and Manufacturing, RIBA Stage 6: Handover and Close Out, RIBA Stage 7: Use |
| Facility | BlockConstructionType | BlockConstructionType | Traditional (load bearing masonry), Steel Frame, Concrete Frame (pre-cast, in-situ), Timber Frame, Modular, Relocatable Mobile, Inflatable, Other |
| Floor | Category | FloorType | Site, Floor or Roof |
| Space | Category | Category-Space | Code: Space name |
| Space | Uniclass | UniclassSL | (from Uniclass SL Spaces/ locations) |
| Zone | ZoneType | ZoneType | Net, Non-net, Net Site or Non-net Site |
| Type | Category | Category-Product | (from Uniclass Pr Products) |
| Type | AssetType | AssetType | Fixed or Movable |
| Type | DurationUnit | DurationUnit | day, minute, month, quarter, week or year |
| System | Category | Category-System | (from Uniclass Ss Systems) Also refer to 5.2.9 System nomenclature |
| Document | Category | DocumentType | (from Uniclass PM Project management) |
| Document | ApprovalBy | ApprovalBy | Owner Approval, Contractor Certified or Information Only |
| Document | Stage | StageType | As Built, Submitted, Approved, Exact Requirement, Maximum Requirement, Minimum Requirement, Requirement |
| Attribute | Category | StageType | As Built, Submitted, Approved, Exact Requirement, Maximum Requirement, Minimum Requirement, Requirement |
| Attribute | SheetName | SheetType | Attribute, Component, Connection, Coordinate, Document, Facility, Floor, Issue, Job, Resource, Space, Spare, System, Type or Zone |
| Attribute | Unit | AttributeUnit | Enumeration, logical, Boolean, %, A, cubicmetres, day, Degrees, each, Gal, gph, gpm, hp, kg, kilometres, kW, lbs, metres, millimetres, MJ, minute, month, pounds, psi, squarekilometres, squaremetres, tonne, tons, UK gallon, V, W, week, year or n/a |
| Attribute - FireRating | Value | FireRating | Undefined, n/a, 20, 30, 60, 90 or 120 |

# 6 Common data environment

## 6.1 Information sharing at tender phase

The project’s common data environment shall be established by the Contractor during the appointment phase. In order to facilitate information sharing with prospective Contractors during the tender phase information will be shared using the following platform:

Information sharing platform at tender stage

Insert name of Electronic Data Management System (EDMS)

All information shared on this platform with the Contractor shall conform to the requirements set out in this Project’s Information Standard with regard to file name, revision and status information. This is to allow the smooth transfer of information from the platform to the project’s common data environment once the Contractor has been appointed. The Contractor is to be granted access to allow them to move relevant information from the information sharing platform to the project’s common data environment as required. The Contractor shall allocate the correct Uniclass PM Project Management code to each information container on transferring the information.

It is to be agreed between the Technical Advisor and the Contractor how the information is transferred but it is recommended that the Technical Advisor provides a completed Task Information Delivery Plan to the Contractor.

## 6.2 Project’s common data environment

DfE require the Contractor to establish (implement, configure, support and manage) the project’s common data environment (CDE) to serve the overall requirements of the project and to support the collaborative production of information for the delivery phase of the project.

The project’s common data environment shall enable:

- each information container to have a unique identifier, using the file naming convention set out in 5.1 File naming, revisions and status of this Project’s Information Standard

- each field to be assigned a value in accordance with the value lists set out in:

  - 5.1.2 Project code

  - 5.1.3 Originator codes

  - 5.1.4 Functional breakdown codes

  - 5.1.5 Spatial breakdown codes

  - 5.1.6 Form codes

  - 5.1.7 Discipline codes

- each information container to have the following attributes assigned:

  - status (suitability) (in accordance with BS EN ISO 19650-2 NA.4.2 and as set out in 5.1.9 Status and revision codes of this Project’s Information Standard)

  - revision (in accordance with BS EN ISO 19650-2 NA.4.3 and as set out in 5.1.9 Status and revision codes of this Project’s Information Standard)

  - Uniclass PM Project management information classification (in accordance with the version set out in 4.5.1 Asset classification of this Project’s Information Standard) – this provides a key to the documentation requirements set out in the Detailed Exchange Information Requirements

  - DEIR ID No to assist with information exchanges

- the ability for information containers to transition between states

- the recording of the name of user and date when information container revisions transition between each state, and

- controlled access at an information container level

The proposed project’s common data environment along with confirmation that it meets (or does not meet) the above requirement shall be provided in the (pre-appointment) BIM Execution Plan.

## 6.3 Distributed common data environments

Delivery team members may wish to use additional common data environments within their own organisations before passing information to the project’s common data environment.

Any distributed common data environments proposed to be used on the project shall be documented in the (pre-appointment) BIM Execution Plan and subsequently the BIM Execution Plan.

Advisory note

There are 2 contract options, delete all advisory notes and the relevant section in green as appropriate:

- Option 1 – JCT D&B Contract for DfE Construction Framework 2025 (CF25)

- Option 2 – Other JCT Contracts (ICD/MWD) – Seek advice from the Legal Counsel for the Scheme

Advisory note

For Option 1 only.

All project information shall be retained in a digital format for a period of 12 years and made available to the DfE on request, including (without limitation):

Information deliverables as required by the project specific Detailed Exchange Information Requirements, and

Information required to be retained under JCT D&B clauses 2.53 (Freedom of Information) and 2.55 (Contractor’s Records)

# 7 Security-minded approach

## 7.1 Outcome of the security triage process

A security triage (ST) process has been undertaken in accordance with BS EN ISO 19650-5 for each project. The outcome of the security triage process is documented here in accordance with BS EN ISO 19650-5 clause 4.8.

Advisory note

Delete as appropriate to retain result of Security Triage process.

Record of the outcome of the security triage process

ST1 Protect sensitive information regarding the project/asset as well as third party sensitive information by applying Clauses 5 to 9 of BS EN ISO 19650-5:2020. ST2 Protect sensitive information regarding the project/asset by applying Clauses 5 to 9 of BS EN ISO 19650-5:2020. ST3 Protect third party sensitive information by applying Clauses 5 to 9 of BS EN ISO 19650-5:2020. Protect any commercial and personal information. ST4 Protect any sensitive commercial and personal information.

## 7.2 Security of information generally

Irrespective of the security triage process, all data and information that DfE needs to collect, store, process, generate or share to deliver services and conduct DfE business has intrinsic value and requires an appropriate degree of protection.

The Contractor and their delivery team has a duty of confidentiality and a responsibility to safeguard all DfE information and/or data that they provide and/or access irrespective of whether it is marked or not.

All files are considered ‘Official’ whether marked or not. Where information is considered sensitive it shall be marked ‘Official Sensitive’.

Refer also to the General Conditions of DfE’s Employer’s Requirements, specifically Section 2.1 which shall be read in conjunction with this Project’s Information Standard. If conflict arises between this resource and the General Conditions, the latter will take precedence.

## 7.3 Disclosure of information

Advisory note

There are 2 contract options, delete all advisory notes and the relevant section in green as appropriate:

- Option 1 – JCT D&B Contract for DfE Construction Framework 2025 (CF25)

- Option 2 – Other JCT Contracts (ICD/MWD) – Seek advice from the Legal Counsel for the Scheme

Information shall only be disclosed in accordance with the provisions of:

Advisory note

For Option 1 only.

JCT D&B clauses 2.51 (Confidentiality and Information Sharing) and 2.53 (Freedom of Information).

## 7.4 Security-minded approach

Where a project has been determined as either ST1, ST2 or ST3 as part of the security triage process, then BS EN ISO 19650-5 clauses 5 to 9 shall be applied. This shall include the provision of a Security Management Plan. Where an ST1, ST2 or ST3 status is determined by the Technical Advisor they shall discuss and agree an approach with the DfE’s Project Manager. It is anticipated that any Security Management Plan would be developed by the DfE or by a specialist Security Consultant.

Any Security Management Plan that is produced shall be incorporated into the appointment between the DfE and the Contractor and subsequently between the Contractor and their delivery team.

# 8 Method of assignment for level of information need

Level of information need is set out in Section 3 of the Exchange Information Requirements and against each information deliverable within the Detailed Exchange Information Requirements. Where the level of information needed is unclear or ambiguous the Contractor shall liaise with the Technical Advisor in the first instance. Where the Technical Advisor is unsure, they shall liaise with the DfE IM Team for further clarification.

The level of information need associated to the Contractor’s exchange information requirements shall be the responsibility of the Contractor.

# 9 Use of information during the operational phase of the asset

The use of information during the operational phase has not been set out in this document.

Information required during the operational phase from the design and construction phase has been set out in detail within the Exchange Information Requirements.

It is expected that information will be managed in accordance with BS EN ISO 19650-3.

Any subsequently produced asset information standard is expected to align with this Project’s Information Standard.

# Appendix A – Operation and Maintenance (O&M) Manual structure

The Operation and Maintenance (O&M) Manual’s purpose is to provide a single source of information for the Responsible Body throughout the lifecycle of the Scheme enabling the user of the manual to obtain any information they require about the Building(s) (Building Elements, Building Services, and Site and Infrastructure).

A comprehensive O&M Manual, following the structure below, shall made be available for review prior to Practical Completion. Any adjustments to the building services systems as part of seasonal commissioning and the Building Performance Evaluation (BPE), shall be added to all copies of the O&M Manual at the end of the Defects Liability/Rectification Period.

The structure of the O&M Manual is suggested below, any alternative structure shall be approved by DfE. For Volumes 2, 3 and 4, the structure shall be applied to each subcontractor package/scope of works.

## Volume 1: Introduction and key information

1.1 Table of contents

1.2 How to use guide

1.3 Description of the Works carried out

1.4 Contact directory

1.5 Health and Safety File

1.6 Building Log Book

1.7 Building User Guide

1.8 All statutory approvals (including planning consents where relevant)

1.9 Training register (recording staff induction)

## Volume 2: Building Elements

An appropriate level of information for each subcontractor package/scope of works relating to the Building Elements (including Architectural, Structural, Catering and FF&E) shall be split into separate sections within Volume 2 and follow the structure below:

1.0 Description of the Works carried out

2.0 Operating instructions and procedures

3.0 Care and maintenance procedures (including 5-year Planned Maintenance Programme)

4.0 Health and Safety information

4.1 Residual risk register

4.2 Health and Safety information relating to any cleaning, maintenance, operation and equipment left on site

4.3 Disposal information

5.0 Manufacturers’ critical spares lists and spares policies

6.0 Warranties and product guarantees

7.0 Testing and commissioning information

8.0 Manufacturers’ information

8.1 Contact directory (names and addresses of contractors, specialists and manufacturers)

8.2 Asset register

8.3 Product information

9.0 Final records

Note: A full suite of Architectural, Structural, Catering, FF&E as-built and as-installed record drawings, models and documents are required.

10.0 On-site modifications (post-contract close)

## Volume 3: Building Services

An appropriate level of information for each subcontractor package/scope of works relating to the Building Services (including Mechanical, Electrical, ICT and Lifts) shall be split into separate sections within Volume 3 and follow the structure below:

1.0 Description of the Works carried out

2.0 Operating instructions and procedures

3.0 Care and maintenance procedures (including 5-year Planned Maintenance Programme)

4.0 Health and Safety information

4.1 Residual risk register

4.2 Health and Safety information relating to any cleaning, maintenance, operation and equipment left on site

4.3 Disposal information

5.0 Manufacturers’ critical spares lists and spares policies

6.0 Warranties and product guarantees

7.0 Testing and commissioning information

8.0 Manufacturers’ information

8.1 Contact directory (names and addresses of contractors, specialists and manufacturers)

8.2 Asset register

8.3 System information

9.0 Final records

Note: A full suite of Mechanical, Electrical, ICT and Lifts as-built and as-installed record drawings, models and documents are required.

10.0 On-site modifications (post-contract close)

## Volume 4: Site and Infrastructure

An appropriate level of information for each subcontractor package/scope of works relating to the Site and Infrastructure (including Civil Engineering and Landscape) shall be split into separate sections within Volume 4 and follow the structure below:

1.0 Description of the Works carried out

2.0 Operating instructions and procedures

3.0 Care and maintenance procedures (including 5-year Planned Maintenance Programme)

4.0 Health and Safety information

4.1 Residual risk register

4.2 Health and Safety information relating to any cleaning, maintenance, operation and equipment left on site

4.3 Disposal information

5.0 Manufacturers’ critical spares lists and spares policies

6.0 Warranties and product guarantees

7.0 Testing and commissioning information

8.0 Manufacturers’ information

8.1 Contact directory (names and addresses of contractors, specialists and manufacturers)

8.2 Asset register

8.3 Product information

9.0 Final records

Note: A full suite of Civil Engineering and Landscape as-built and as-installed record including drawings, models and documents are required.

10.0 On-site modifications (post-contract close)

# Appendix B – Health and Safety File structure

The Health and Safety File shall be included in Volume 1: Introduction and key information of the Operation and Maintenance (O&M) Manual.

BSRIA Building Guide 1 2009 sets out the type of information the Health and Safety File shall contain. The file is a repository of health and safety information that serves as a legal record, benefiting both clients and end users – from initial construction through use, cleaning, maintenance, alterations and refurbishment, and demolition. The file shall not include things that will be of no help when planning future construction work such as pre-construction information, the construction phase plan, contractual documents etc.

The structure of the Health and Safety File is suggested below, any alternative structure shall be approved by DfE and satisfy Appendix 4 of Health and Safety Executive’s ‘Managing health and safety in construction’ guidance document and comply with the Construction (Design and Management) Regulations 2015:

1.0 Purpose of the Health and Safety File

2.0 Introduction

2.1 Table of contents

2.2 How to use guide

2.3 Emergency information

3.0 Brief description of the Works carried out

4.0 Contact directory

5.0 Health and Safety information

5.1 Residual hazards

5.2 Access arrangements and equipment for cleaning and maintenance

5.3 Information regarding the removal or dismantling of installed plant and equipment

5.4 Services information

5.5 Hazardous materials used

5.6 Asbestos

5.7 Key structural principles and safe working loads

5.8 Relevant survey information

5.9 Fire Safety Management Plan

5.10 Legionella risk assessment and log book

5.11 Local Exhaust Ventilation (LEV) log book

5.12 Workplace Exposure Limits (WEL)

5.13 Fume cupboard risk assessment to HSG 258

6.0 Final record schedules

6.1 Architectural: schedules of all as-built and as-installed final records

6.2 Structural: schedules of all as-built and as-installed final records

6.3 Catering: schedules of all as-built and as-installed final records

6.4 FF&E: schedules of all as-built and as-installed final records

6.5 Building Services: schedules of all as-built and as-installed final records

6.5.1 Mechanical Services: schedules of all as-built and as-installed final records

6.5.2 Electrical Services: schedules of all as-built and as-installed final records

6.5.3 ICT: schedules of all as-built and as-installed final records

6.5.4 Lifts: schedules of all as-built and as-installed final records

6.6 Civil Engineering: schedules of all as-built and as-installed final records

6.7 Landscape: schedules of all as-built and as-installed final records

Note: Includes Drawings, Models and Documents for all of the above.

# Appendix C – Building Log Book Structure

A Building Log Book shall be included in Volume 1: Introduction and key information of the Operation and Maintenance (O&M) Manual.

The Contractor shall prepare summary information about the New Building(s) or Refurbished/Remodelled Building(s), its Building Services and all maintenance requirements in a comprehensive Building Log Book, for compliance with Building Regulations Part L 2021. CIBSE TM31 sets out the type of information the Building Log Book shall contain. It covers how a building is intended to work and how it is to be maintained and serviced. It also provides a means to record the energy use and maintenance of the services within the Building(s).

The structure of the Building Log Book is suggested below, any alternative structure shall be approved by DfE:

1.0 Building history

2.0 Purpose and description of responsibilities

3.0 Links to other key documents

4.0 Main contacts

5.0 Commissioning, handover and compliance

6.0 Overall building design

7.0 Summary of areas and occupancy

8.0 Summary of main building services plant

9.0 Overview of controls/Building Management System (BMS)

10.0 Occupant information

11.0 Metering, monitoring and targeting strategy

12.0 Building energy performance records

13.0 Maintenance review

14.0 Results of in-use investigations

Appendix: Relevant compliance and test certificates

# Appendix D – Building User Guide Structure

A Building User Guide shall be included in Volume 1: Introduction and key information of the Operation and Maintenance (O&M) Manual.

The Building User Guide shall be provided in a format (electronic and hard copy) suitable for the Responsible Body to use on a day-to-day basis and as a separate document to the rest of the Operation and Maintenance (O&M) Manual. A sample shall be provided for review prior to Practical Completion and shall include comprehensive quick reference sections for all building management instructions and solutions.

BSRIA Building Guide 26 2011 sets out the type of information the Building User Guide shall contain. It shall provide a comprehensive description of all building elements and systems that can be controlled or adjusted by the usual occupant of a room within the school/college building. It shall describe in easily understandable, non-technical language how normal day-to-day operation and function is to be achieved.

The structure of the Building User Guide is suggested below, any alternative structure shall be approved by DfE:

1.0 Building information

1.1 General

2.0 Emergency information

2.1 Fire response and alarm system

2.2 Fire Safety Management Plan

2.3 First aid

3.0 Building utility and environmental

3.1 Building services

Ventilation (including any specialist systems installed in kitchens, science laboratories, D&T workshops etc)

Heating

Building Management System

Cooling

Domestic hot and cold water

Gas (normal operation and emergency shut off and resetting in science laboratories and kitchens)

Lighting (manual and automatic controls for electric lighting and use of blinds to control daylighting and glare)

Small power systems

Security system (intercoms/alarm systems)

Public Address/Visual Audio Systems

ICT

Telephone

Lifts

3.2 Energy and environmental strategy

Summary of the operational rationale for each of the above services installed

Issues relating to the zoning of services

Potential operational interactions (such as between ventilation and cooling)

Occupant actions required, such as keeping manually operated ventilation open at night to enable free cooling in summer

3.3 Annual building energy consumption

3.4 Energy conservation

Benchmark energy consumption targets

Practical steps occupants can take to control and reduce energy consumption (such as minimising cold draughts through open doors)

3.5 Controls (BMS)

What they look like

Where they are located

What they control

How they achieve control (with details of local outside settings)

When the occupants should use them

Feedback on the status (such as lamps and read outs)

Special considerations (such as default status (on, off, standby) and relationship of any automatic settings, such as window closure during rain)

3.6 Communications

3.7 Commercial kitchen

4.0 Water management

4.1 Water strategy

4.2 Domestic water

5.0 Materials and waste (post-handover or contract close)

5.1 Materials purchasing policy

5.2 Waste management policy

6.0 Transport facilities

6.1 Transport

6.2 Parking

7.0 Refit and rearrangement considerations

7.1 Refit building/building sections

7.2 Rearrangement/addition of furniture

8.0 Reporting provision

8.1 Reporting procedures

8.2 Responsible parties

9.0 Training

9.1 Compulsory training

9.2 Additional training

Note: Where training is provided to demonstrate functional controls, a digital video file of the training shall be provided in a format suitable for upload onto the school/college intranet.

© Crown copyright 2026

This publication is licensed under the terms of the Open Government Licence v3.0, except where otherwise stated. To view this licence, visit nationalarchives.gov.uk/doc/open-government-licence/version/3.

Where we have identified any third-party copyright information, you will need to obtain permission from the copyright holders concerned.

About this publication:

enquiries  https://www.gov.uk/contact-dfe

download 	www.gov.uk/government/publications

Follow us on Twitter: @educationgovuk
Connect with us on Facebook: facebook.com/educationgovuk

When not using the DfE Construction Framework 2025, seek appropriate advice on how the DfE’s Employer’s Requirements can be incorporated into the relevant Contract(s).

Where this document has been incorporated into a Scheme Contract, the version which is incorporated at the date of that Scheme Contract shall apply under the terms of that Scheme Contract, unless varied in accordance with the terms of the relevant Scheme Contract.

When not using the DfE Construction Framework, seek appropriate advice on how the DfE’s Employer’s Requirements can be incorporated into the relevant Contract(s).

The standards listed here generally align to the requirements of the UK BIM Framework. BS 8536:2022 ‘Design, manufacture and construction for operability - Code of practice’ is not specifically referenced although the DfE’s Soft Landings process is aligned. DfE reserves its right to amend the Project’s Information Standard to require the use of any updated standard within the BS EN ISO 19650 suite, when published, following the process outlined in the Framework Agreement.

Incorporating corrigendum February 2021.

Security triage process will be applied as a minimum.

Contractors and associated delivery teams may use the current published version BS EN ISO 16739-1:2024 (IFC4.3 ADD2) in lieu of PAS/ISO 16739:2005 (IFC2x3 TC1) if appropriate. This will rely on software solutions across the delivery team supporting the ability to export and import this version as required. Note: Changing the version used will require amendment to other parts of the Project’s Information Standard, particularly with respect to 5.2.8 Object nomenclature – Occurrence. Where BS EN ISO 16739-1:2024 is appropriate for delivery, the Contractor shall confirm the required changes in their (pre-appointment) BIM Execution Plan during the tender response phase.

Used for COBie CreatedOn on all sheets.

There is no requirement for NRM to be provided within models although the Contractor and their delivery team may wish to include these for their own needs.

DfE’s requirement is for three characters. The use of two characters up to six characters would be subject to DfE approval.

These Uniclass Ro Roles codes have been taken from the April 2025 release.

File names shall use the form code value set out within the Detailed Exchange Information Requirements

As per ISO 19650, for information containers with complex forms, the principal form shall be used unless specified otherwise in the Project’s Information Standard.

DfE’s requirement is for one character. The use of two characters would be subject to DfE approval.

The ‘Originator’ code is used to distinguish different organisations with the same ‘Discipline’ code.

BS EN ISO 7200: 2004 identifies 'document status' as optional, status codes are not mandated on title blocks. Contractors are permitted to manage status effectively via their CDE or issue documents directly from the supply chain to the Contractor with S5 as the status. This complies with ISO 19650 workflows using watermarks and metadata, avoiding intermediate reissues (e.g., S2, S3, S4 and S5).

The information shall be used on relevant project information and the exact values here shall be provided in the completed information including IFC-SPFs and COBie file(s).

The information shall be used on relevant project information and the exact values here shall be provided in the completed information including IFC-SPFs and COBie file(s).

The information shall be used on relevant project information and the exact values here shall be provided in the completed information including IFC-SPFs and COBie file(s).

Zone Names are set out as categories of space that make up net and non-net area within Building Bulletins 103 and 104 for Spaces and Places. The information in this table shall be used as the basis for populating the Zone workbook of COBie.

These Uniclass Ss Systems codes have been taken from the April 2025 release.

Replace ‘[UserDefined]’ with an appropriate name (in PascalCase) including omitting the square brackets.

This includes both Spaces and Places.

There are two permissible workflows for updating the status and revision for accepted information for sharing at tender phase which in order of preference are as follows:

i) update the EDMS metadata columns

ii) update the Information Container file name

Document Control tables shall be updated to reflect this change or watermarked/stamped to indicate that the metadata or file name takes precedence. Where it is not possible to edit the file (e.g., models) the metadata/file name shall take precedence.

The status code is not required in documentation title blocks.

ST is the abbreviated term for “security triage”.

Including details of the Design, Construction and Post-construction team.

Refer to Appendix B for Health and Safety File structure.

Refer to Appendix C for Building Log Book structure.

Refer to Appendix D for Building User Guide structure.

Including requirements for demolition, decommissioning and disposal.

Including requirements for demolition, decommissioning and disposal.

Including requirements for demolition, decommissioning and disposal.